## TIPS
TIPS:
1. This matrix is a micro clash detection matrix intended to reduce the number of false positives and increase confidence in clash results, leading to pathways to automate the process of digital coordination.
2. This matrix is to be used by Services teams and Project Managers to instruct the BIM team to prioritise and execute clash detection tasks.
3. Matrix snapshot and explanation:
Selection B list of Items Categories
Clash Task Priority - refer to Clash Matrix Legend
Selection A list of Items Categories
Clearance factors - refer to Clash Matrix Legend
4. Workflow:
Start with the Clash Matrix and refer back to the Clash Matrix Legend
Use the Clash Task (Output) to filter by task priority and copy the associated task into the coordination software (such as Revizto)
[Imporntant] | After updating the clash matrix, please click 'Refresh All'are refreshed under the 'Clash Task Output' section

## Clash Matrix (Update to suit)
Selection A (A) | Selection (B) | ARC_Columns* | ARC_Ceiling | ARC_Doors* | ARC_Gen Model & Casework* | ARC_Roof | ARC_Fire & Acoustic Wall | ARC_Windows | ARC_Services Walkway | ARC_Accessible Path | SRV_Access Panel | ARC_Lighting Fixtures | ARC_Plumbing Fixtures | ARC_SOG Floor Insulation | STR_Seismic Elements | STR_Conc work Excl Floor Slab | STR_Steelwork (Bracing and Columns) | STR Floor | HYD_Uninsulated Pipes and Acc | HYD_Pipe Insulation | HYD_Uninsulated Hot and Cold Pipes and Acc | HYD_Hot and Cold Insulation | HYD_Plumbing Fixture | MEC_Air Terminals | MEC_Uninsulated Duct and Acc | MEC_Duct Insulation | MEC_Pipe Insulation | MEC_Uninsulated Pipes and Acc | MEC_Uninulated Flexi duct | MEC_Equipment | ELE_Cable Tray and Fittings | ELE_Conduit* | ELE_Electrical Equip. | ELE_Small Devices | ELE_Services Lighting Fixtures | FIR_Fire Pipes | FIR_Sprinklers Heads | FIR_Heat or Smoke Detectors
ARC_Columns*
ARC_Ceiling |  |  |  | T2 |  |  | T2 | [11 empty] | T2 | T2 | T2 | T2 | T2 |  | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 |  | T2
|  |  |  | HC |  |  | HC | [11 empty] | C100V | C100V | C100V | C100V | C100V |  | C100V | C100V | C100V | C100V | C100V | C100V | C100V | C100V | C100V | C100V |  | C100V
ARC_Doors* | [8 empty] | T3 | [6 empty] | T2 | T2 | T2 | [5 empty] | T2 | [5 empty] | T2 |  |  | T3
[9 empty] | HC | [6 empty] | HC | HC | HC | [5 empty] | C50 | [5 empty] | C50 |  |  | HC
ARC_Gen Model & Casework* | [6 empty] | T4 | T4 | T4 |  | T4 |  | T4 |  | T4 | T4 | T4 | T4 | T4 | T4 | T4 | T4 | T4 | T4 | T4 | T4 | T4 | T4 | T4 | T4 | T4 | T4 | T4 | T4 | T4 | T4
[7 empty] | HC | HC | HC |  | HC |  | HC |  | HC | HC | HC | HC | HC | HC | HC | HC | HC | HC | HC | HC | HC | HC | HC | HC | HC | HC | HC | HC | HC | HC
ARC_Roof
ARC_Fire & Acoustic Wall | [10 empty] | T2 |  |  |  | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 |  | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 |  | T2 | T2
[11 empty] | C50 |  |  |  | HC | HC | HC | HC | C50 | C50 | C50 | C50 | C50 |  | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 |  | C50 | C50
ARC_Windows | [15 empty] | T2 | T2 | T2
[16 empty] | HC | HC | HC
ARC_Services Walkway | [10 empty] | T3 |  | T3 | T3 | T3 | T3 | T3 | T3 | T3 | T3 | T3 | T3 | T3 | T3 | T3 | T3 | T3 | T3 | T3 | T3 | T3 | T3 | T3 | T3 | T3 | T3 | T3 | T3
[11 empty] | HC |  | HC | HC | HC | HC | HC | HC | HC | HC | HC | HC | HC | HC | HC | HC | HC | HC | HC | HC | HC | HC | HC | HC | HC | HC | HC | HC
ARC_Accessible Path
SRV_Access Panel | [12 empty] | T3 |  | T3 |  | T3 |  | T3 | T3 | T3 | T3 |  | T3 | T3 | T3 | T3 | T3 | T3 | T3 | T3 | T3 | T3 | T3 | T3 | T3
[13 empty] | C600V |  | C600V |  | C600V |  | C600V | C600V | C600V | C600V |  | C600V | C600V | C600V | C600V | C600V | C600V | C600V | C600V | C600V | C600V | C600V | C600V | C600V
ARC_Lighting Fixtures | [34 empty] | T3
HC
ARC_Plumbing Fixtures | [14 empty] | T3 | T3 | T3 |  | T3 | T3 | T3 | T3 | T3 | T3 | T3 | T3 | T3 | T3 | T3 | T3 | T3 | T3 | T3 | T3 | T3
[15 empty] | C50 | C50 | C50 |  | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50
ARC_SOG Floor Insulation | [18 empty] | T1 | T1 | T1 | T1 | T1 | T1 | T1 | T1 | T1 | T1 | T1 | T1 | T1 | T1 | T1 |  |  | T1
[19 empty] | HC | HC | HC | HC | HC | HC | HC | HC | HC | HC | HC | HC | HC | HC | HC |  |  | HC
STR_Seismic Elements | [15 empty] | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2
[16 empty] | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50
STR_Conc work Excl Floor Slab | [18 empty] | T1 | T1 | T1 | T1 | T1 | T1 | T1 | T1 | T1 | T1 | T1 | T1 | T1 | T1 | T1 | T1 | T1 | T1
[19 empty] | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50
STR_Steelwork (Bracing and Columns) | [18 empty] | T1 | T1 | T1 | T1 |  | T1 | T1 | T1 | T1 | T1 | T1 | T1 | T1 | T1 | T1 | T1 | T1
[19 empty] | C50 | C50 | C50 | C50 |  | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50
STR Floor | [18 empty] | T1 | T1 | T1 | T1 |  | T1 | T1 | T1 | T1 | T1 | T1 | T1 | T1 | T1 | T1 | T1 | T1 | T1
[19 empty] | C50 | C50 | C50 | C50 |  | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50
HYD_Uninsulated Pipes and Acc | [19 empty] | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2
[20 empty] | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50
HYD_Pipe Insulation | [20 empty] | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2
[21 empty] | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50
HYD_Uninsulated Hot and Cold Pipes and Acc | [21 empty] | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2
[22 empty] | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50
HYD_Hot and Cold Insulation | [22 empty] | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2
[23 empty] | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50
HYD_Plumbing Fixture | [23 empty] | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2
[24 empty] | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50
MEC_Air Terminals | [24 empty] | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2
[25 empty] | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C1500
MEC_Uninsulated Duct and Acc | [25 empty] | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2
[26 empty] | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50
MEC_Duct Insulation | [26 empty] | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2
[27 empty] | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50
MEC_Pipe Insulation | [27 empty] | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2
[28 empty] | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50
MEC_Uninsulated Pipes and Acc | [28 empty] | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2 | T2
[29 empty] | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50
MEC_Uninulated Flexi duct | [29 empty] | T2 | T2 | T2 | T2 | T2 | T2 | T2
[30 empty] | C50 | C50 | C50 | C50 | C50 | C50 | C50
MEC_Equipment | [30 empty] | T3 | T3 | T3 | T3 | T3 | T3 | T3 | T3
[31 empty] | C50 | C50 | C50 | C50 | C50 | C50 | C50 | C50
ELE_Cable Tray and Fittings | [30 empty] | T3 | T3 | T3 | T3 | T3 | T3 | T3 | T3
[31 empty] | C150 | C50 | C50 | C50 | C50 | C50 | C50 | C50
ELE_Conduit* | [32 empty] | T3 | T3 | T3 | T3 | T3 | T3
[33 empty] | C50 | C50 | C50 | C50 | C50 | C50
ELE_Electrical Equip. | [33 empty] | T3 | T3 | T2 | T3 | T3
[34 empty] | C50 | C50 | C50 | C50 | C1500
ELE_Small Devices | [33 empty] | T3 | T3 | T3 | T3 | T3
[34 empty] | C50 | C50 | C50 | C50 | C50
ELE_Services Lighting Fixtures | [34 empty] | T3 | T3 | T3 | T3
[35 empty] | C50 | C50 | C50 | C50
FIR_Fire Pipes | [36 empty] | T2 | T2
[37 empty] | C50 | C50
FIR_Sprinklers Heads | [36 empty] | T3 | T3
[37 empty] | HC | C1500
FIR_Heat or Smoke Detectors | [37 empty] | T3
HC

## Rawdata (Do not edit)
Clash Task Category | Clearance | Selection A | Selection B | Clash Task Name
0 | 0 | ARC_Columns* | ARC_Columns* | NL-0-ARC_Columns* vs ARC_Columns*
0 | 0 | ARC_Columns* | ARC_Ceiling | NL-0-ARC_Columns* vs ARC_Ceiling
0 | 0 | ARC_Columns* | ARC_Doors* | NL-0-ARC_Columns* vs ARC_Doors*
0 | 0 | ARC_Columns* | ARC_Gen Model & Casework* | NL-0-ARC_Columns* vs ARC_Gen Model & Casework*
0 | 0 | ARC_Columns* | ARC_Roof | NL-0-ARC_Columns* vs ARC_Roof
0 | 0 | ARC_Columns* | ARC_Fire & Acoustic Wall | NL-0-ARC_Columns* vs ARC_Fire & Acoustic Wall
0 | 0 | ARC_Columns* | ARC_Windows | NL-0-ARC_Columns* vs ARC_Windows
0 | 0 | ARC_Columns* | ARC_Services Walkway | NL-0-ARC_Columns* vs ARC_Services Walkway
0 | 0 | ARC_Columns* | ARC_Accessible Path | NL-0-ARC_Columns* vs ARC_Accessible Path
0 | 0 | ARC_Columns* | SRV_Access Panel | NL-0-ARC_Columns* vs SRV_Access Panel
0 | 0 | ARC_Columns* | ARC_Lighting Fixtures | NL-0-ARC_Columns* vs ARC_Lighting Fixtures
0 | 0 | ARC_Columns* | ARC_Plumbing Fixtures | NL-0-ARC_Columns* vs ARC_Plumbing Fixtures
0 | 0 | ARC_Columns* | ARC_SOG Floor Insulation | NL-0-ARC_Columns* vs ARC_SOG Floor Insulation
0 | 0 | ARC_Columns* | STR_Seismic Elements | NL-0-ARC_Columns* vs STR_Seismic Elements
0 | 0 | ARC_Columns* | STR_Conc work Excl Floor Slab | NL-0-ARC_Columns* vs STR_Conc work Excl Floor Slab
0 | 0 | ARC_Columns* | STR_Steelwork (Bracing and Columns) | NL-0-ARC_Columns* vs STR_Steelwork (Bracing and Columns)
0 | 0 | ARC_Columns* | STR Floor | NL-0-ARC_Columns* vs STR Floor
0 | 0 | ARC_Columns* | HYD_Uninsulated Pipes and Acc | NL-0-ARC_Columns* vs HYD_Uninsulated Pipes and Acc
0 | 0 | ARC_Columns* | HYD_Pipe Insulation | NL-0-ARC_Columns* vs HYD_Pipe Insulation
0 | 0 | ARC_Columns* | HYD_Uninsulated Hot and Cold Pipes and Acc | NL-0-ARC_Columns* vs HYD_Uninsulated Hot and Cold Pipes and Acc
0 | 0 | ARC_Columns* | HYD_Hot and Cold Insulation | NL-0-ARC_Columns* vs HYD_Hot and Cold Insulation
0 | 0 | ARC_Columns* | HYD_Plumbing Fixture | NL-0-ARC_Columns* vs HYD_Plumbing Fixture
0 | 0 | ARC_Columns* | MEC_Air Terminals | NL-0-ARC_Columns* vs MEC_Air Terminals
0 | 0 | ARC_Columns* | MEC_Uninsulated Duct and Acc | NL-0-ARC_Columns* vs MEC_Uninsulated Duct and Acc
0 | 0 | ARC_Columns* | MEC_Duct Insulation | NL-0-ARC_Columns* vs MEC_Duct Insulation
0 | 0 | ARC_Columns* | MEC_Pipe Insulation | NL-0-ARC_Columns* vs MEC_Pipe Insulation
0 | 0 | ARC_Columns* | MEC_Uninsulated Pipes and Acc | NL-0-ARC_Columns* vs MEC_Uninsulated Pipes and Acc
0 | 0 | ARC_Columns* | MEC_Uninulated Flexi duct | NL-0-ARC_Columns* vs MEC_Uninulated Flexi duct
0 | 0 | ARC_Columns* | MEC_Equipment | NL-0-ARC_Columns* vs MEC_Equipment
0 | 0 | ARC_Columns* | ELE_Cable Tray and Fittings | NL-0-ARC_Columns* vs ELE_Cable Tray and Fittings
0 | 0 | ARC_Columns* | ELE_Conduit* | NL-0-ARC_Columns* vs ELE_Conduit*
0 | 0 | ARC_Columns* | ELE_Electrical Equip. | NL-0-ARC_Columns* vs ELE_Electrical Equip.
0 | 0 | ARC_Columns* | ELE_Small Devices | NL-0-ARC_Columns* vs ELE_Small Devices
0 | 0 | ARC_Columns* | ELE_Services Lighting Fixtures | NL-0-ARC_Columns* vs ELE_Services Lighting Fixtures
0 | 0 | ARC_Columns* | FIR_Fire Pipes | NL-0-ARC_Columns* vs FIR_Fire Pipes
0 | 0 | ARC_Columns* | FIR_Sprinklers Heads | NL-0-ARC_Columns* vs FIR_Sprinklers Heads
0 | 0 | ARC_Columns* | FIR_Heat or Smoke Detectors | NL-0-ARC_Columns* vs FIR_Heat or Smoke Detectors
0 | 0 | ARC_Ceiling | ARC_Ceiling | NL-0-ARC_Ceiling vs ARC_Ceiling
T2 | HC | ARC_Ceiling | ARC_Doors* | NL-HC-ARC_Ceiling vs ARC_Doors*
0 | 0 | ARC_Ceiling | ARC_Gen Model & Casework* | NL-0-ARC_Ceiling vs ARC_Gen Model & Casework*
0 | 0 | ARC_Ceiling | ARC_Roof | NL-0-ARC_Ceiling vs ARC_Roof
T2 | HC | ARC_Ceiling | ARC_Fire & Acoustic Wall | NL-HC-ARC_Ceiling vs ARC_Fire & Acoustic Wall
0 | 0 | ARC_Ceiling | ARC_Windows | NL-0-ARC_Ceiling vs ARC_Windows
0 | 0 | ARC_Ceiling | ARC_Services Walkway | NL-0-ARC_Ceiling vs ARC_Services Walkway
0 | 0 | ARC_Ceiling | ARC_Accessible Path | NL-0-ARC_Ceiling vs ARC_Accessible Path
0 | 0 | ARC_Ceiling | SRV_Access Panel | NL-0-ARC_Ceiling vs SRV_Access Panel
0 | 0 | ARC_Ceiling | ARC_Lighting Fixtures | NL-0-ARC_Ceiling vs ARC_Lighting Fixtures
0 | 0 | ARC_Ceiling | ARC_Plumbing Fixtures | NL-0-ARC_Ceiling vs ARC_Plumbing Fixtures
0 | 0 | ARC_Ceiling | ARC_SOG Floor Insulation | NL-0-ARC_Ceiling vs ARC_SOG Floor Insulation
0 | 0 | ARC_Ceiling | STR_Seismic Elements | NL-0-ARC_Ceiling vs STR_Seismic Elements
0 | 0 | ARC_Ceiling | STR_Conc work Excl Floor Slab | NL-0-ARC_Ceiling vs STR_Conc work Excl Floor Slab
0 | 0 | ARC_Ceiling | STR_Steelwork (Bracing and Columns) | NL-0-ARC_Ceiling vs STR_Steelwork (Bracing and Columns)
0 | 0 | ARC_Ceiling | STR Floor | NL-0-ARC_Ceiling vs STR Floor
T2 | C100V | ARC_Ceiling | HYD_Uninsulated Pipes and Acc | NL-C100V-ARC_Ceiling vs HYD_Uninsulated Pipes and Acc
T2 | C100V | ARC_Ceiling | HYD_Pipe Insulation | NL-C100V-ARC_Ceiling vs HYD_Pipe Insulation
T2 | C100V | ARC_Ceiling | HYD_Uninsulated Hot and Cold Pipes and Acc | NL-C100V-ARC_Ceiling vs HYD_Uninsulated Hot and Cold Pipes and Acc
T2 | C100V | ARC_Ceiling | HYD_Hot and Cold Insulation | NL-C100V-ARC_Ceiling vs HYD_Hot and Cold Insulation
T2 | C100V | ARC_Ceiling | HYD_Plumbing Fixture | NL-C100V-ARC_Ceiling vs HYD_Plumbing Fixture
0 | 0 | ARC_Ceiling | MEC_Air Terminals | NL-0-ARC_Ceiling vs MEC_Air Terminals
T2 | C100V | ARC_Ceiling | MEC_Uninsulated Duct and Acc | NL-C100V-ARC_Ceiling vs MEC_Uninsulated Duct and Acc
T2 | C100V | ARC_Ceiling | MEC_Duct Insulation | NL-C100V-ARC_Ceiling vs MEC_Duct Insulation
T2 | C100V | ARC_Ceiling | MEC_Pipe Insulation | NL-C100V-ARC_Ceiling vs MEC_Pipe Insulation
T2 | C100V | ARC_Ceiling | MEC_Uninsulated Pipes and Acc | NL-C100V-ARC_Ceiling vs MEC_Uninsulated Pipes and Acc
T2 | C100V | ARC_Ceiling | MEC_Uninulated Flexi duct | NL-C100V-ARC_Ceiling vs MEC_Uninulated Flexi duct
T2 | C100V | ARC_Ceiling | MEC_Equipment | NL-C100V-ARC_Ceiling vs MEC_Equipment
T2 | C100V | ARC_Ceiling | ELE_Cable Tray and Fittings | NL-C100V-ARC_Ceiling vs ELE_Cable Tray and Fittings
T2 | C100V | ARC_Ceiling | ELE_Conduit* | NL-C100V-ARC_Ceiling vs ELE_Conduit*
T2 | C100V | ARC_Ceiling | ELE_Electrical Equip. | NL-C100V-ARC_Ceiling vs ELE_Electrical Equip.
T2 | C100V | ARC_Ceiling | ELE_Small Devices | NL-C100V-ARC_Ceiling vs ELE_Small Devices
0 | 0 | ARC_Ceiling | ELE_Services Lighting Fixtures | NL-0-ARC_Ceiling vs ELE_Services Lighting Fixtures
T2 | C100V | ARC_Ceiling | FIR_Fire Pipes | NL-C100V-ARC_Ceiling vs FIR_Fire Pipes
0 | 0 | ARC_Ceiling | FIR_Sprinklers Heads | NL-0-ARC_Ceiling vs FIR_Sprinklers Heads
0 | 0 | ARC_Ceiling | FIR_Heat or Smoke Detectors | NL-0-ARC_Ceiling vs FIR_Heat or Smoke Detectors
0 | 0 | ARC_Doors* | ARC_Doors* | NL-0-ARC_Doors* vs ARC_Doors*
0 | 0 | ARC_Doors* | ARC_Gen Model & Casework* | NL-0-ARC_Doors* vs ARC_Gen Model & Casework*
0 | 0 | ARC_Doors* | ARC_Roof | NL-0-ARC_Doors* vs ARC_Roof
0 | 0 | ARC_Doors* | ARC_Fire & Acoustic Wall | NL-0-ARC_Doors* vs ARC_Fire & Acoustic Wall
0 | 0 | ARC_Doors* | ARC_Windows | NL-0-ARC_Doors* vs ARC_Windows
T3 | HC | ARC_Doors* | ARC_Services Walkway | NL-HC-ARC_Doors* vs ARC_Services Walkway
0 | 0 | ARC_Doors* | ARC_Accessible Path | NL-0-ARC_Doors* vs ARC_Accessible Path
0 | 0 | ARC_Doors* | SRV_Access Panel | NL-0-ARC_Doors* vs SRV_Access Panel
0 | 0 | ARC_Doors* | ARC_Lighting Fixtures | NL-0-ARC_Doors* vs ARC_Lighting Fixtures
0 | 0 | ARC_Doors* | ARC_Plumbing Fixtures | NL-0-ARC_Doors* vs ARC_Plumbing Fixtures
0 | 0 | ARC_Doors* | ARC_SOG Floor Insulation | NL-0-ARC_Doors* vs ARC_SOG Floor Insulation
0 | 0 | ARC_Doors* | STR_Seismic Elements | NL-0-ARC_Doors* vs STR_Seismic Elements
T2 | HC | ARC_Doors* | STR_Conc work Excl Floor Slab | NL-HC-ARC_Doors* vs STR_Conc work Excl Floor Slab
T2 | HC | ARC_Doors* | STR_Steelwork (Bracing and Columns) | NL-HC-ARC_Doors* vs STR_Steelwork (Bracing and Columns)
T2 | HC | ARC_Doors* | STR Floor | NL-HC-ARC_Doors* vs STR Floor
0 | 0 | ARC_Doors* | HYD_Uninsulated Pipes and Acc | NL-0-ARC_Doors* vs HYD_Uninsulated Pipes and Acc
0 | 0 | ARC_Doors* | HYD_Pipe Insulation | NL-0-ARC_Doors* vs HYD_Pipe Insulation
0 | 0 | ARC_Doors* | HYD_Uninsulated Hot and Cold Pipes and Acc | NL-0-ARC_Doors* vs HYD_Uninsulated Hot and Cold Pipes and Acc
0 | 0 | ARC_Doors* | HYD_Hot and Cold Insulation | NL-0-ARC_Doors* vs HYD_Hot and Cold Insulation
0 | 0 | ARC_Doors* | HYD_Plumbing Fixture | NL-0-ARC_Doors* vs HYD_Plumbing Fixture
T2 | C50 | ARC_Doors* | MEC_Air Terminals | NL-C50-ARC_Doors* vs MEC_Air Terminals
0 | 0 | ARC_Doors* | MEC_Uninsulated Duct and Acc | NL-0-ARC_Doors* vs MEC_Uninsulated Duct and Acc
0 | 0 | ARC_Doors* | MEC_Duct Insulation | NL-0-ARC_Doors* vs MEC_Duct Insulation
0 | 0 | ARC_Doors* | MEC_Pipe Insulation | NL-0-ARC_Doors* vs MEC_Pipe Insulation
0 | 0 | ARC_Doors* | MEC_Uninsulated Pipes and Acc | NL-0-ARC_Doors* vs MEC_Uninsulated Pipes and Acc
0 | 0 | ARC_Doors* | MEC_Uninulated Flexi duct | NL-0-ARC_Doors* vs MEC_Uninulated Flexi duct
T2 | C50 | ARC_Doors* | MEC_Equipment | NL-C50-ARC_Doors* vs MEC_Equipment
0 | 0 | ARC_Doors* | ELE_Cable Tray and Fittings | NL-0-ARC_Doors* vs ELE_Cable Tray and Fittings
0 | 0 | ARC_Doors* | ELE_Conduit* | NL-0-ARC_Doors* vs ELE_Conduit*
T3 | HC | ARC_Doors* | ELE_Electrical Equip. | NL-HC-ARC_Doors* vs ELE_Electrical Equip.
0 | 0 | ARC_Doors* | ELE_Small Devices | NL-0-ARC_Doors* vs ELE_Small Devices
0 | 0 | ARC_Doors* | ELE_Services Lighting Fixtures | NL-0-ARC_Doors* vs ELE_Services Lighting Fixtures
0 | 0 | ARC_Doors* | FIR_Fire Pipes | NL-0-ARC_Doors* vs FIR_Fire Pipes
0 | 0 | ARC_Doors* | FIR_Sprinklers Heads | NL-0-ARC_Doors* vs FIR_Sprinklers Heads
0 | 0 | ARC_Doors* | FIR_Heat or Smoke Detectors | NL-0-ARC_Doors* vs FIR_Heat or Smoke Detectors
0 | 0 | ARC_Gen Model & Casework* | ARC_Gen Model & Casework* | NL-0-ARC_Gen Model & Casework* vs ARC_Gen Model & Casework*
0 | 0 | ARC_Gen Model & Casework* | ARC_Roof | NL-0-ARC_Gen Model & Casework* vs ARC_Roof
T4 | HC | ARC_Gen Model & Casework* | ARC_Fire & Acoustic Wall | NL-HC-ARC_Gen Model & Casework* vs ARC_Fire & Acoustic Wall
T4 | HC | ARC_Gen Model & Casework* | ARC_Windows | NL-HC-ARC_Gen Model & Casework* vs ARC_Windows
T4 | HC | ARC_Gen Model & Casework* | ARC_Services Walkway | NL-HC-ARC_Gen Model & Casework* vs ARC_Services Walkway
0 | 0 | ARC_Gen Model & Casework* | ARC_Accessible Path | NL-0-ARC_Gen Model & Casework* vs ARC_Accessible Path
T4 | HC | ARC_Gen Model & Casework* | SRV_Access Panel | NL-HC-ARC_Gen Model & Casework* vs SRV_Access Panel
0 | 0 | ARC_Gen Model & Casework* | ARC_Lighting Fixtures | NL-0-ARC_Gen Model & Casework* vs ARC_Lighting Fixtures
T4 | HC | ARC_Gen Model & Casework* | ARC_Plumbing Fixtures | NL-HC-ARC_Gen Model & Casework* vs ARC_Plumbing Fixtures
0 | 0 | ARC_Gen Model & Casework* | ARC_SOG Floor Insulation | NL-0-ARC_Gen Model & Casework* vs ARC_SOG Floor Insulation
T4 | HC | ARC_Gen Model & Casework* | STR_Seismic Elements | NL-HC-ARC_Gen Model & Casework* vs STR_Seismic Elements
T4 | HC | ARC_Gen Model & Casework* | STR_Conc work Excl Floor Slab | NL-HC-ARC_Gen Model & Casework* vs STR_Conc work Excl Floor Slab
T4 | HC | ARC_Gen Model & Casework* | STR_Steelwork (Bracing and Columns) | NL-HC-ARC_Gen Model & Casework* vs STR_Steelwork (Bracing and Columns)
T4 | HC | ARC_Gen Model & Casework* | STR Floor | NL-HC-ARC_Gen Model & Casework* vs STR Floor
T4 | HC | ARC_Gen Model & Casework* | HYD_Uninsulated Pipes and Acc | NL-HC-ARC_Gen Model & Casework* vs HYD_Uninsulated Pipes and Acc
T4 | HC | ARC_Gen Model & Casework* | HYD_Pipe Insulation | NL-HC-ARC_Gen Model & Casework* vs HYD_Pipe Insulation
T4 | HC | ARC_Gen Model & Casework* | HYD_Uninsulated Hot and Cold Pipes and Acc | NL-HC-ARC_Gen Model & Casework* vs HYD_Uninsulated Hot and Cold Pipes and Acc
T4 | HC | ARC_Gen Model & Casework* | HYD_Hot and Cold Insulation | NL-HC-ARC_Gen Model & Casework* vs HYD_Hot and Cold Insulation
T4 | HC | ARC_Gen Model & Casework* | HYD_Plumbing Fixture | NL-HC-ARC_Gen Model & Casework* vs HYD_Plumbing Fixture
T4 | HC | ARC_Gen Model & Casework* | MEC_Air Terminals | NL-HC-ARC_Gen Model & Casework* vs MEC_Air Terminals
T4 | HC | ARC_Gen Model & Casework* | MEC_Uninsulated Duct and Acc | NL-HC-ARC_Gen Model & Casework* vs MEC_Uninsulated Duct and Acc
T4 | HC | ARC_Gen Model & Casework* | MEC_Duct Insulation | NL-HC-ARC_Gen Model & Casework* vs MEC_Duct Insulation
T4 | HC | ARC_Gen Model & Casework* | MEC_Pipe Insulation | NL-HC-ARC_Gen Model & Casework* vs MEC_Pipe Insulation
T4 | HC | ARC_Gen Model & Casework* | MEC_Uninsulated Pipes and Acc | NL-HC-ARC_Gen Model & Casework* vs MEC_Uninsulated Pipes and Acc
T4 | HC | ARC_Gen Model & Casework* | MEC_Uninulated Flexi duct | NL-HC-ARC_Gen Model & Casework* vs MEC_Uninulated Flexi duct
T4 | HC | ARC_Gen Model & Casework* | MEC_Equipment | NL-HC-ARC_Gen Model & Casework* vs MEC_Equipment
T4 | HC | ARC_Gen Model & Casework* | ELE_Cable Tray and Fittings | NL-HC-ARC_Gen Model & Casework* vs ELE_Cable Tray and Fittings
T4 | HC | ARC_Gen Model & Casework* | ELE_Conduit* | NL-HC-ARC_Gen Model & Casework* vs ELE_Conduit*
T4 | HC | ARC_Gen Model & Casework* | ELE_Electrical Equip. | NL-HC-ARC_Gen Model & Casework* vs ELE_Electrical Equip.
T4 | HC | ARC_Gen Model & Casework* | ELE_Small Devices | NL-HC-ARC_Gen Model & Casework* vs ELE_Small Devices
T4 | HC | ARC_Gen Model & Casework* | ELE_Services Lighting Fixtures | NL-HC-ARC_Gen Model & Casework* vs ELE_Services Lighting Fixtures
T4 | HC | ARC_Gen Model & Casework* | FIR_Fire Pipes | NL-HC-ARC_Gen Model & Casework* vs FIR_Fire Pipes
0 | 0 | ARC_Gen Model & Casework* | FIR_Sprinklers Heads | NL-0-ARC_Gen Model & Casework* vs FIR_Sprinklers Heads
0 | 0 | ARC_Gen Model & Casework* | FIR_Heat or Smoke Detectors | NL-0-ARC_Gen Model & Casework* vs FIR_Heat or Smoke Detectors
0 | 0 | ARC_Roof | ARC_Roof | NL-0-ARC_Roof vs ARC_Roof
0 | 0 | ARC_Roof | ARC_Fire & Acoustic Wall | NL-0-ARC_Roof vs ARC_Fire & Acoustic Wall
0 | 0 | ARC_Roof | ARC_Windows | NL-0-ARC_Roof vs ARC_Windows
0 | 0 | ARC_Roof | ARC_Services Walkway | NL-0-ARC_Roof vs ARC_Services Walkway
0 | 0 | ARC_Roof | ARC_Accessible Path | NL-0-ARC_Roof vs ARC_Accessible Path
0 | 0 | ARC_Roof | SRV_Access Panel | NL-0-ARC_Roof vs SRV_Access Panel
0 | 0 | ARC_Roof | ARC_Lighting Fixtures | NL-0-ARC_Roof vs ARC_Lighting Fixtures
0 | 0 | ARC_Roof | ARC_Plumbing Fixtures | NL-0-ARC_Roof vs ARC_Plumbing Fixtures
0 | 0 | ARC_Roof | ARC_SOG Floor Insulation | NL-0-ARC_Roof vs ARC_SOG Floor Insulation
0 | 0 | ARC_Roof | STR_Seismic Elements | NL-0-ARC_Roof vs STR_Seismic Elements
0 | 0 | ARC_Roof | STR_Conc work Excl Floor Slab | NL-0-ARC_Roof vs STR_Conc work Excl Floor Slab
0 | 0 | ARC_Roof | STR_Steelwork (Bracing and Columns) | NL-0-ARC_Roof vs STR_Steelwork (Bracing and Columns)
0 | 0 | ARC_Roof | STR Floor | NL-0-ARC_Roof vs STR Floor
0 | 0 | ARC_Roof | HYD_Uninsulated Pipes and Acc | NL-0-ARC_Roof vs HYD_Uninsulated Pipes and Acc
0 | 0 | ARC_Roof | HYD_Pipe Insulation | NL-0-ARC_Roof vs HYD_Pipe Insulation
0 | 0 | ARC_Roof | HYD_Uninsulated Hot and Cold Pipes and Acc | NL-0-ARC_Roof vs HYD_Uninsulated Hot and Cold Pipes and Acc
0 | 0 | ARC_Roof | HYD_Hot and Cold Insulation | NL-0-ARC_Roof vs HYD_Hot and Cold Insulation
0 | 0 | ARC_Roof | HYD_Plumbing Fixture | NL-0-ARC_Roof vs HYD_Plumbing Fixture
0 | 0 | ARC_Roof | MEC_Air Terminals | NL-0-ARC_Roof vs MEC_Air Terminals
0 | 0 | ARC_Roof | MEC_Uninsulated Duct and Acc | NL-0-ARC_Roof vs MEC_Uninsulated Duct and Acc
0 | 0 | ARC_Roof | MEC_Duct Insulation | NL-0-ARC_Roof vs MEC_Duct Insulation
0 | 0 | ARC_Roof | MEC_Pipe Insulation | NL-0-ARC_Roof vs MEC_Pipe Insulation
0 | 0 | ARC_Roof | MEC_Uninsulated Pipes and Acc | NL-0-ARC_Roof vs MEC_Uninsulated Pipes and Acc
0 | 0 | ARC_Roof | MEC_Uninulated Flexi duct | NL-0-ARC_Roof vs MEC_Uninulated Flexi duct
0 | 0 | ARC_Roof | MEC_Equipment | NL-0-ARC_Roof vs MEC_Equipment
0 | 0 | ARC_Roof | ELE_Cable Tray and Fittings | NL-0-ARC_Roof vs ELE_Cable Tray and Fittings
0 | 0 | ARC_Roof | ELE_Conduit* | NL-0-ARC_Roof vs ELE_Conduit*
0 | 0 | ARC_Roof | ELE_Electrical Equip. | NL-0-ARC_Roof vs ELE_Electrical Equip.
0 | 0 | ARC_Roof | ELE_Small Devices | NL-0-ARC_Roof vs ELE_Small Devices
0 | 0 | ARC_Roof | ELE_Services Lighting Fixtures | NL-0-ARC_Roof vs ELE_Services Lighting Fixtures
0 | 0 | ARC_Roof | FIR_Fire Pipes | NL-0-ARC_Roof vs FIR_Fire Pipes
0 | 0 | ARC_Roof | FIR_Sprinklers Heads | NL-0-ARC_Roof vs FIR_Sprinklers Heads
0 | 0 | ARC_Roof | FIR_Heat or Smoke Detectors | NL-0-ARC_Roof vs FIR_Heat or Smoke Detectors
0 | 0 | ARC_Fire & Acoustic Wall | ARC_Fire & Acoustic Wall | NL-0-ARC_Fire & Acoustic Wall vs ARC_Fire & Acoustic Wall
0 | 0 | ARC_Fire & Acoustic Wall | ARC_Windows | NL-0-ARC_Fire & Acoustic Wall vs ARC_Windows
0 | 0 | ARC_Fire & Acoustic Wall | ARC_Services Walkway | NL-0-ARC_Fire & Acoustic Wall vs ARC_Services Walkway
0 | 0 | ARC_Fire & Acoustic Wall | ARC_Accessible Path | NL-0-ARC_Fire & Acoustic Wall vs ARC_Accessible Path
T2 | C50 | ARC_Fire & Acoustic Wall | SRV_Access Panel | NL-C50-ARC_Fire & Acoustic Wall vs SRV_Access Panel
0 | 0 | ARC_Fire & Acoustic Wall | ARC_Lighting Fixtures | NL-0-ARC_Fire & Acoustic Wall vs ARC_Lighting Fixtures
0 | 0 | ARC_Fire & Acoustic Wall | ARC_Plumbing Fixtures | NL-0-ARC_Fire & Acoustic Wall vs ARC_Plumbing Fixtures
0 | 0 | ARC_Fire & Acoustic Wall | ARC_SOG Floor Insulation | NL-0-ARC_Fire & Acoustic Wall vs ARC_SOG Floor Insulation
T2 | HC | ARC_Fire & Acoustic Wall | STR_Seismic Elements | NL-HC-ARC_Fire & Acoustic Wall vs STR_Seismic Elements
T2 | HC | ARC_Fire & Acoustic Wall | STR_Conc work Excl Floor Slab | NL-HC-ARC_Fire & Acoustic Wall vs STR_Conc work Excl Floor Slab
T2 | HC | ARC_Fire & Acoustic Wall | STR_Steelwork (Bracing and Columns) | NL-HC-ARC_Fire & Acoustic Wall vs STR_Steelwork (Bracing and Columns)
T2 | HC | ARC_Fire & Acoustic Wall | STR Floor | NL-HC-ARC_Fire & Acoustic Wall vs STR Floor
T2 | C50 | ARC_Fire & Acoustic Wall | HYD_Uninsulated Pipes and Acc | NL-C50-ARC_Fire & Acoustic Wall vs HYD_Uninsulated Pipes and Acc
T2 | C50 | ARC_Fire & Acoustic Wall | HYD_Pipe Insulation | NL-C50-ARC_Fire & Acoustic Wall vs HYD_Pipe Insulation
T2 | C50 | ARC_Fire & Acoustic Wall | HYD_Uninsulated Hot and Cold Pipes and Acc | NL-C50-ARC_Fire & Acoustic Wall vs HYD_Uninsulated Hot and Cold Pipes and Acc
T2 | C50 | ARC_Fire & Acoustic Wall | HYD_Hot and Cold Insulation | NL-C50-ARC_Fire & Acoustic Wall vs HYD_Hot and Cold Insulation
T2 | C50 | ARC_Fire & Acoustic Wall | HYD_Plumbing Fixture | NL-C50-ARC_Fire & Acoustic Wall vs HYD_Plumbing Fixture
0 | 0 | ARC_Fire & Acoustic Wall | MEC_Air Terminals | NL-0-ARC_Fire & Acoustic Wall vs MEC_Air Terminals
T2 | C50 | ARC_Fire & Acoustic Wall | MEC_Uninsulated Duct and Acc | NL-C50-ARC_Fire & Acoustic Wall vs MEC_Uninsulated Duct and Acc
T2 | C50 | ARC_Fire & Acoustic Wall | MEC_Duct Insulation | NL-C50-ARC_Fire & Acoustic Wall vs MEC_Duct Insulation
T2 | C50 | ARC_Fire & Acoustic Wall | MEC_Pipe Insulation | NL-C50-ARC_Fire & Acoustic Wall vs MEC_Pipe Insulation
T2 | C50 | ARC_Fire & Acoustic Wall | MEC_Uninsulated Pipes and Acc | NL-C50-ARC_Fire & Acoustic Wall vs MEC_Uninsulated Pipes and Acc
T2 | C50 | ARC_Fire & Acoustic Wall | MEC_Uninulated Flexi duct | NL-C50-ARC_Fire & Acoustic Wall vs MEC_Uninulated Flexi duct
T2 | C50 | ARC_Fire & Acoustic Wall | MEC_Equipment | NL-C50-ARC_Fire & Acoustic Wall vs MEC_Equipment
T2 | C50 | ARC_Fire & Acoustic Wall | ELE_Cable Tray and Fittings | NL-C50-ARC_Fire & Acoustic Wall vs ELE_Cable Tray and Fittings
T2 | C50 | ARC_Fire & Acoustic Wall | ELE_Conduit* | NL-C50-ARC_Fire & Acoustic Wall vs ELE_Conduit*
T2 | C50 | ARC_Fire & Acoustic Wall | ELE_Electrical Equip. | NL-C50-ARC_Fire & Acoustic Wall vs ELE_Electrical Equip.
0 | 0 | ARC_Fire & Acoustic Wall | ELE_Small Devices | NL-0-ARC_Fire & Acoustic Wall vs ELE_Small Devices
T2 | C50 | ARC_Fire & Acoustic Wall | ELE_Services Lighting Fixtures | NL-C50-ARC_Fire & Acoustic Wall vs ELE_Services Lighting Fixtures
T2 | C50 | ARC_Fire & Acoustic Wall | FIR_Fire Pipes | NL-C50-ARC_Fire & Acoustic Wall vs FIR_Fire Pipes
0 | 0 | ARC_Fire & Acoustic Wall | FIR_Sprinklers Heads | NL-0-ARC_Fire & Acoustic Wall vs FIR_Sprinklers Heads
0 | 0 | ARC_Fire & Acoustic Wall | FIR_Heat or Smoke Detectors | NL-0-ARC_Fire & Acoustic Wall vs FIR_Heat or Smoke Detectors
0 | 0 | ARC_Windows | ARC_Windows | NL-0-ARC_Windows vs ARC_Windows
0 | 0 | ARC_Windows | ARC_Services Walkway | NL-0-ARC_Windows vs ARC_Services Walkway
0 | 0 | ARC_Windows | ARC_Accessible Path | NL-0-ARC_Windows vs ARC_Accessible Path
0 | 0 | ARC_Windows | SRV_Access Panel | NL-0-ARC_Windows vs SRV_Access Panel
0 | 0 | ARC_Windows | ARC_Lighting Fixtures | NL-0-ARC_Windows vs ARC_Lighting Fixtures
0 | 0 | ARC_Windows | ARC_Plumbing Fixtures | NL-0-ARC_Windows vs ARC_Plumbing Fixtures
0 | 0 | ARC_Windows | ARC_SOG Floor Insulation | NL-0-ARC_Windows vs ARC_SOG Floor Insulation
0 | 0 | ARC_Windows | STR_Seismic Elements | NL-0-ARC_Windows vs STR_Seismic Elements
T2 | HC | ARC_Windows | STR_Conc work Excl Floor Slab | NL-HC-ARC_Windows vs STR_Conc work Excl Floor Slab
T2 | HC | ARC_Windows | STR_Steelwork (Bracing and Columns) | NL-HC-ARC_Windows vs STR_Steelwork (Bracing and Columns)
T2 | HC | ARC_Windows | STR Floor | NL-HC-ARC_Windows vs STR Floor
0 | 0 | ARC_Windows | HYD_Uninsulated Pipes and Acc | NL-0-ARC_Windows vs HYD_Uninsulated Pipes and Acc
0 | 0 | ARC_Windows | HYD_Pipe Insulation | NL-0-ARC_Windows vs HYD_Pipe Insulation
0 | 0 | ARC_Windows | HYD_Uninsulated Hot and Cold Pipes and Acc | NL-0-ARC_Windows vs HYD_Uninsulated Hot and Cold Pipes and Acc
0 | 0 | ARC_Windows | HYD_Hot and Cold Insulation | NL-0-ARC_Windows vs HYD_Hot and Cold Insulation
0 | 0 | ARC_Windows | HYD_Plumbing Fixture | NL-0-ARC_Windows vs HYD_Plumbing Fixture
0 | 0 | ARC_Windows | MEC_Air Terminals | NL-0-ARC_Windows vs MEC_Air Terminals
0 | 0 | ARC_Windows | MEC_Uninsulated Duct and Acc | NL-0-ARC_Windows vs MEC_Uninsulated Duct and Acc
0 | 0 | ARC_Windows | MEC_Duct Insulation | NL-0-ARC_Windows vs MEC_Duct Insulation
0 | 0 | ARC_Windows | MEC_Pipe Insulation | NL-0-ARC_Windows vs MEC_Pipe Insulation
0 | 0 | ARC_Windows | MEC_Uninsulated Pipes and Acc | NL-0-ARC_Windows vs MEC_Uninsulated Pipes and Acc
0 | 0 | ARC_Windows | MEC_Uninulated Flexi duct | NL-0-ARC_Windows vs MEC_Uninulated Flexi duct
0 | 0 | ARC_Windows | MEC_Equipment | NL-0-ARC_Windows vs MEC_Equipment
0 | 0 | ARC_Windows | ELE_Cable Tray and Fittings | NL-0-ARC_Windows vs ELE_Cable Tray and Fittings
0 | 0 | ARC_Windows | ELE_Conduit* | NL-0-ARC_Windows vs ELE_Conduit*
0 | 0 | ARC_Windows | ELE_Electrical Equip. | NL-0-ARC_Windows vs ELE_Electrical Equip.
0 | 0 | ARC_Windows | ELE_Small Devices | NL-0-ARC_Windows vs ELE_Small Devices
0 | 0 | ARC_Windows | ELE_Services Lighting Fixtures | NL-0-ARC_Windows vs ELE_Services Lighting Fixtures
0 | 0 | ARC_Windows | FIR_Fire Pipes | NL-0-ARC_Windows vs FIR_Fire Pipes
0 | 0 | ARC_Windows | FIR_Sprinklers Heads | NL-0-ARC_Windows vs FIR_Sprinklers Heads
0 | 0 | ARC_Windows | FIR_Heat or Smoke Detectors | NL-0-ARC_Windows vs FIR_Heat or Smoke Detectors
0 | 0 | ARC_Services Walkway | ARC_Services Walkway | NL-0-ARC_Services Walkway vs ARC_Services Walkway
0 | 0 | ARC_Services Walkway | ARC_Accessible Path | NL-0-ARC_Services Walkway vs ARC_Accessible Path
T3 | HC | ARC_Services Walkway | SRV_Access Panel | NL-HC-ARC_Services Walkway vs SRV_Access Panel
0 | 0 | ARC_Services Walkway | ARC_Lighting Fixtures | NL-0-ARC_Services Walkway vs ARC_Lighting Fixtures
T3 | HC | ARC_Services Walkway | ARC_Plumbing Fixtures | NL-HC-ARC_Services Walkway vs ARC_Plumbing Fixtures
T3 | HC | ARC_Services Walkway | ARC_SOG Floor Insulation | NL-HC-ARC_Services Walkway vs ARC_SOG Floor Insulation
T3 | HC | ARC_Services Walkway | STR_Seismic Elements | NL-HC-ARC_Services Walkway vs STR_Seismic Elements
T3 | HC | ARC_Services Walkway | STR_Conc work Excl Floor Slab | NL-HC-ARC_Services Walkway vs STR_Conc work Excl Floor Slab
T3 | HC | ARC_Services Walkway | STR_Steelwork (Bracing and Columns) | NL-HC-ARC_Services Walkway vs STR_Steelwork (Bracing and Columns)
T3 | HC | ARC_Services Walkway | STR Floor | NL-HC-ARC_Services Walkway vs STR Floor
T3 | HC | ARC_Services Walkway | HYD_Uninsulated Pipes and Acc | NL-HC-ARC_Services Walkway vs HYD_Uninsulated Pipes and Acc
T3 | HC | ARC_Services Walkway | HYD_Pipe Insulation | NL-HC-ARC_Services Walkway vs HYD_Pipe Insulation
T3 | HC | ARC_Services Walkway | HYD_Uninsulated Hot and Cold Pipes and Acc | NL-HC-ARC_Services Walkway vs HYD_Uninsulated Hot and Cold Pipes and Acc
T3 | HC | ARC_Services Walkway | HYD_Hot and Cold Insulation | NL-HC-ARC_Services Walkway vs HYD_Hot and Cold Insulation
T3 | HC | ARC_Services Walkway | HYD_Plumbing Fixture | NL-HC-ARC_Services Walkway vs HYD_Plumbing Fixture
T3 | HC | ARC_Services Walkway | MEC_Air Terminals | NL-HC-ARC_Services Walkway vs MEC_Air Terminals
T3 | HC | ARC_Services Walkway | MEC_Uninsulated Duct and Acc | NL-HC-ARC_Services Walkway vs MEC_Uninsulated Duct and Acc
T3 | HC | ARC_Services Walkway | MEC_Duct Insulation | NL-HC-ARC_Services Walkway vs MEC_Duct Insulation
T3 | HC | ARC_Services Walkway | MEC_Pipe Insulation | NL-HC-ARC_Services Walkway vs MEC_Pipe Insulation
T3 | HC | ARC_Services Walkway | MEC_Uninsulated Pipes and Acc | NL-HC-ARC_Services Walkway vs MEC_Uninsulated Pipes and Acc
T3 | HC | ARC_Services Walkway | MEC_Uninulated Flexi duct | NL-HC-ARC_Services Walkway vs MEC_Uninulated Flexi duct
T3 | HC | ARC_Services Walkway | MEC_Equipment | NL-HC-ARC_Services Walkway vs MEC_Equipment
T3 | HC | ARC_Services Walkway | ELE_Cable Tray and Fittings | NL-HC-ARC_Services Walkway vs ELE_Cable Tray and Fittings
T3 | HC | ARC_Services Walkway | ELE_Conduit* | NL-HC-ARC_Services Walkway vs ELE_Conduit*
T3 | HC | ARC_Services Walkway | ELE_Electrical Equip. | NL-HC-ARC_Services Walkway vs ELE_Electrical Equip.
T3 | HC | ARC_Services Walkway | ELE_Small Devices | NL-HC-ARC_Services Walkway vs ELE_Small Devices
T3 | HC | ARC_Services Walkway | ELE_Services Lighting Fixtures | NL-HC-ARC_Services Walkway vs ELE_Services Lighting Fixtures
T3 | HC | ARC_Services Walkway | FIR_Fire Pipes | NL-HC-ARC_Services Walkway vs FIR_Fire Pipes
T3 | HC | ARC_Services Walkway | FIR_Sprinklers Heads | NL-HC-ARC_Services Walkway vs FIR_Sprinklers Heads
T3 | HC | ARC_Services Walkway | FIR_Heat or Smoke Detectors | NL-HC-ARC_Services Walkway vs FIR_Heat or Smoke Detectors
0 | 0 | ARC_Accessible Path | ARC_Accessible Path | NL-0-ARC_Accessible Path vs ARC_Accessible Path
0 | 0 | ARC_Accessible Path | SRV_Access Panel | NL-0-ARC_Accessible Path vs SRV_Access Panel
0 | 0 | ARC_Accessible Path | ARC_Lighting Fixtures | NL-0-ARC_Accessible Path vs ARC_Lighting Fixtures
0 | 0 | ARC_Accessible Path | ARC_Plumbing Fixtures | NL-0-ARC_Accessible Path vs ARC_Plumbing Fixtures
0 | 0 | ARC_Accessible Path | ARC_SOG Floor Insulation | NL-0-ARC_Accessible Path vs ARC_SOG Floor Insulation
0 | 0 | ARC_Accessible Path | STR_Seismic Elements | NL-0-ARC_Accessible Path vs STR_Seismic Elements
0 | 0 | ARC_Accessible Path | STR_Conc work Excl Floor Slab | NL-0-ARC_Accessible Path vs STR_Conc work Excl Floor Slab
0 | 0 | ARC_Accessible Path | STR_Steelwork (Bracing and Columns) | NL-0-ARC_Accessible Path vs STR_Steelwork (Bracing and Columns)
0 | 0 | ARC_Accessible Path | STR Floor | NL-0-ARC_Accessible Path vs STR Floor
0 | 0 | ARC_Accessible Path | HYD_Uninsulated Pipes and Acc | NL-0-ARC_Accessible Path vs HYD_Uninsulated Pipes and Acc
0 | 0 | ARC_Accessible Path | HYD_Pipe Insulation | NL-0-ARC_Accessible Path vs HYD_Pipe Insulation
0 | 0 | ARC_Accessible Path | HYD_Uninsulated Hot and Cold Pipes and Acc | NL-0-ARC_Accessible Path vs HYD_Uninsulated Hot and Cold Pipes and Acc
0 | 0 | ARC_Accessible Path | HYD_Hot and Cold Insulation | NL-0-ARC_Accessible Path vs HYD_Hot and Cold Insulation
0 | 0 | ARC_Accessible Path | HYD_Plumbing Fixture | NL-0-ARC_Accessible Path vs HYD_Plumbing Fixture
0 | 0 | ARC_Accessible Path | MEC_Air Terminals | NL-0-ARC_Accessible Path vs MEC_Air Terminals
0 | 0 | ARC_Accessible Path | MEC_Uninsulated Duct and Acc | NL-0-ARC_Accessible Path vs MEC_Uninsulated Duct and Acc
0 | 0 | ARC_Accessible Path | MEC_Duct Insulation | NL-0-ARC_Accessible Path vs MEC_Duct Insulation
0 | 0 | ARC_Accessible Path | MEC_Pipe Insulation | NL-0-ARC_Accessible Path vs MEC_Pipe Insulation
0 | 0 | ARC_Accessible Path | MEC_Uninsulated Pipes and Acc | NL-0-ARC_Accessible Path vs MEC_Uninsulated Pipes and Acc
0 | 0 | ARC_Accessible Path | MEC_Uninulated Flexi duct | NL-0-ARC_Accessible Path vs MEC_Uninulated Flexi duct
0 | 0 | ARC_Accessible Path | MEC_Equipment | NL-0-ARC_Accessible Path vs MEC_Equipment
0 | 0 | ARC_Accessible Path | ELE_Cable Tray and Fittings | NL-0-ARC_Accessible Path vs ELE_Cable Tray and Fittings
0 | 0 | ARC_Accessible Path | ELE_Conduit* | NL-0-ARC_Accessible Path vs ELE_Conduit*
0 | 0 | ARC_Accessible Path | ELE_Electrical Equip. | NL-0-ARC_Accessible Path vs ELE_Electrical Equip.
0 | 0 | ARC_Accessible Path | ELE_Small Devices | NL-0-ARC_Accessible Path vs ELE_Small Devices
0 | 0 | ARC_Accessible Path | ELE_Services Lighting Fixtures | NL-0-ARC_Accessible Path vs ELE_Services Lighting Fixtures
0 | 0 | ARC_Accessible Path | FIR_Fire Pipes | NL-0-ARC_Accessible Path vs FIR_Fire Pipes
0 | 0 | ARC_Accessible Path | FIR_Sprinklers Heads | NL-0-ARC_Accessible Path vs FIR_Sprinklers Heads
0 | 0 | ARC_Accessible Path | FIR_Heat or Smoke Detectors | NL-0-ARC_Accessible Path vs FIR_Heat or Smoke Detectors
0 | 0 | SRV_Access Panel | SRV_Access Panel | NL-0-SRV_Access Panel vs SRV_Access Panel
0 | 0 | SRV_Access Panel | ARC_Lighting Fixtures | NL-0-SRV_Access Panel vs ARC_Lighting Fixtures
T3 | C600V | SRV_Access Panel | ARC_Plumbing Fixtures | NL-C600V-SRV_Access Panel vs ARC_Plumbing Fixtures
0 | 0 | SRV_Access Panel | ARC_SOG Floor Insulation | NL-0-SRV_Access Panel vs ARC_SOG Floor Insulation
T3 | C600V | SRV_Access Panel | STR_Seismic Elements | NL-C600V-SRV_Access Panel vs STR_Seismic Elements
0 | 0 | SRV_Access Panel | STR_Conc work Excl Floor Slab | NL-0-SRV_Access Panel vs STR_Conc work Excl Floor Slab
T3 | C600V | SRV_Access Panel | STR_Steelwork (Bracing and Columns) | NL-C600V-SRV_Access Panel vs STR_Steelwork (Bracing and Columns)
0 | 0 | SRV_Access Panel | STR Floor | NL-0-SRV_Access Panel vs STR Floor
T3 | C600V | SRV_Access Panel | HYD_Uninsulated Pipes and Acc | NL-C600V-SRV_Access Panel vs HYD_Uninsulated Pipes and Acc
T3 | C600V | SRV_Access Panel | HYD_Pipe Insulation | NL-C600V-SRV_Access Panel vs HYD_Pipe Insulation
T3 | C600V | SRV_Access Panel | HYD_Uninsulated Hot and Cold Pipes and Acc | NL-C600V-SRV_Access Panel vs HYD_Uninsulated Hot and Cold Pipes and Acc
T3 | C600V | SRV_Access Panel | HYD_Hot and Cold Insulation | NL-C600V-SRV_Access Panel vs HYD_Hot and Cold Insulation
0 | 0 | SRV_Access Panel | HYD_Plumbing Fixture | NL-0-SRV_Access Panel vs HYD_Plumbing Fixture
T3 | C600V | SRV_Access Panel | MEC_Air Terminals | NL-C600V-SRV_Access Panel vs MEC_Air Terminals
T3 | C600V | SRV_Access Panel | MEC_Uninsulated Duct and Acc | NL-C600V-SRV_Access Panel vs MEC_Uninsulated Duct and Acc
T3 | C600V | SRV_Access Panel | MEC_Duct Insulation | NL-C600V-SRV_Access Panel vs MEC_Duct Insulation
T3 | C600V | SRV_Access Panel | MEC_Pipe Insulation | NL-C600V-SRV_Access Panel vs MEC_Pipe Insulation
T3 | C600V | SRV_Access Panel | MEC_Uninsulated Pipes and Acc | NL-C600V-SRV_Access Panel vs MEC_Uninsulated Pipes and Acc
T3 | C600V | SRV_Access Panel | MEC_Uninulated Flexi duct | NL-C600V-SRV_Access Panel vs MEC_Uninulated Flexi duct
T3 | C600V | SRV_Access Panel | MEC_Equipment | NL-C600V-SRV_Access Panel vs MEC_Equipment
T3 | C600V | SRV_Access Panel | ELE_Cable Tray and Fittings | NL-C600V-SRV_Access Panel vs ELE_Cable Tray and Fittings
T3 | C600V | SRV_Access Panel | ELE_Conduit* | NL-C600V-SRV_Access Panel vs ELE_Conduit*
T3 | C600V | SRV_Access Panel | ELE_Electrical Equip. | NL-C600V-SRV_Access Panel vs ELE_Electrical Equip.
T3 | C600V | SRV_Access Panel | ELE_Small Devices | NL-C600V-SRV_Access Panel vs ELE_Small Devices
T3 | C600V | SRV_Access Panel | ELE_Services Lighting Fixtures | NL-C600V-SRV_Access Panel vs ELE_Services Lighting Fixtures
T3 | C600V | SRV_Access Panel | FIR_Fire Pipes | NL-C600V-SRV_Access Panel vs FIR_Fire Pipes
0 | 0 | SRV_Access Panel | FIR_Sprinklers Heads | NL-0-SRV_Access Panel vs FIR_Sprinklers Heads
0 | 0 | SRV_Access Panel | FIR_Heat or Smoke Detectors | NL-0-SRV_Access Panel vs FIR_Heat or Smoke Detectors
0 | 0 | ARC_Lighting Fixtures | ARC_Lighting Fixtures | NL-0-ARC_Lighting Fixtures vs ARC_Lighting Fixtures
0 | 0 | ARC_Lighting Fixtures | ARC_Plumbing Fixtures | NL-0-ARC_Lighting Fixtures vs ARC_Plumbing Fixtures
0 | 0 | ARC_Lighting Fixtures | ARC_SOG Floor Insulation | NL-0-ARC_Lighting Fixtures vs ARC_SOG Floor Insulation
0 | 0 | ARC_Lighting Fixtures | STR_Seismic Elements | NL-0-ARC_Lighting Fixtures vs STR_Seismic Elements
0 | 0 | ARC_Lighting Fixtures | STR_Conc work Excl Floor Slab | NL-0-ARC_Lighting Fixtures vs STR_Conc work Excl Floor Slab
0 | 0 | ARC_Lighting Fixtures | STR_Steelwork (Bracing and Columns) | NL-0-ARC_Lighting Fixtures vs STR_Steelwork (Bracing and Columns)
0 | 0 | ARC_Lighting Fixtures | STR Floor | NL-0-ARC_Lighting Fixtures vs STR Floor
0 | 0 | ARC_Lighting Fixtures | HYD_Uninsulated Pipes and Acc | NL-0-ARC_Lighting Fixtures vs HYD_Uninsulated Pipes and Acc
0 | 0 | ARC_Lighting Fixtures | HYD_Pipe Insulation | NL-0-ARC_Lighting Fixtures vs HYD_Pipe Insulation
0 | 0 | ARC_Lighting Fixtures | HYD_Uninsulated Hot and Cold Pipes and Acc | NL-0-ARC_Lighting Fixtures vs HYD_Uninsulated Hot and Cold Pipes and Acc
0 | 0 | ARC_Lighting Fixtures | HYD_Hot and Cold Insulation | NL-0-ARC_Lighting Fixtures vs HYD_Hot and Cold Insulation
0 | 0 | ARC_Lighting Fixtures | HYD_Plumbing Fixture | NL-0-ARC_Lighting Fixtures vs HYD_Plumbing Fixture
0 | 0 | ARC_Lighting Fixtures | MEC_Air Terminals | NL-0-ARC_Lighting Fixtures vs MEC_Air Terminals
0 | 0 | ARC_Lighting Fixtures | MEC_Uninsulated Duct and Acc | NL-0-ARC_Lighting Fixtures vs MEC_Uninsulated Duct and Acc
0 | 0 | ARC_Lighting Fixtures | MEC_Duct Insulation | NL-0-ARC_Lighting Fixtures vs MEC_Duct Insulation
0 | 0 | ARC_Lighting Fixtures | MEC_Pipe Insulation | NL-0-ARC_Lighting Fixtures vs MEC_Pipe Insulation
0 | 0 | ARC_Lighting Fixtures | MEC_Uninsulated Pipes and Acc | NL-0-ARC_Lighting Fixtures vs MEC_Uninsulated Pipes and Acc
0 | 0 | ARC_Lighting Fixtures | MEC_Uninulated Flexi duct | NL-0-ARC_Lighting Fixtures vs MEC_Uninulated Flexi duct
0 | 0 | ARC_Lighting Fixtures | MEC_Equipment | NL-0-ARC_Lighting Fixtures vs MEC_Equipment
0 | 0 | ARC_Lighting Fixtures | ELE_Cable Tray and Fittings | NL-0-ARC_Lighting Fixtures vs ELE_Cable Tray and Fittings
0 | 0 | ARC_Lighting Fixtures | ELE_Conduit* | NL-0-ARC_Lighting Fixtures vs ELE_Conduit*
0 | 0 | ARC_Lighting Fixtures | ELE_Electrical Equip. | NL-0-ARC_Lighting Fixtures vs ELE_Electrical Equip.
0 | 0 | ARC_Lighting Fixtures | ELE_Small Devices | NL-0-ARC_Lighting Fixtures vs ELE_Small Devices
T3 | HC | ARC_Lighting Fixtures | ELE_Services Lighting Fixtures | NL-HC-ARC_Lighting Fixtures vs ELE_Services Lighting Fixtures
0 | 0 | ARC_Lighting Fixtures | FIR_Fire Pipes | NL-0-ARC_Lighting Fixtures vs FIR_Fire Pipes
0 | 0 | ARC_Lighting Fixtures | FIR_Sprinklers Heads | NL-0-ARC_Lighting Fixtures vs FIR_Sprinklers Heads
0 | 0 | ARC_Lighting Fixtures | FIR_Heat or Smoke Detectors | NL-0-ARC_Lighting Fixtures vs FIR_Heat or Smoke Detectors
0 | 0 | ARC_Plumbing Fixtures | ARC_Plumbing Fixtures | NL-0-ARC_Plumbing Fixtures vs ARC_Plumbing Fixtures
0 | 0 | ARC_Plumbing Fixtures | ARC_SOG Floor Insulation | NL-0-ARC_Plumbing Fixtures vs ARC_SOG Floor Insulation
T3 | C50 | ARC_Plumbing Fixtures | STR_Seismic Elements | NL-C50-ARC_Plumbing Fixtures vs STR_Seismic Elements
T3 | C50 | ARC_Plumbing Fixtures | STR_Conc work Excl Floor Slab | NL-C50-ARC_Plumbing Fixtures vs STR_Conc work Excl Floor Slab
T3 | C50 | ARC_Plumbing Fixtures | STR_Steelwork (Bracing and Columns) | NL-C50-ARC_Plumbing Fixtures vs STR_Steelwork (Bracing and Columns)
0 | 0 | ARC_Plumbing Fixtures | STR Floor | NL-0-ARC_Plumbing Fixtures vs STR Floor
T3 | C50 | ARC_Plumbing Fixtures | HYD_Uninsulated Pipes and Acc | NL-C50-ARC_Plumbing Fixtures vs HYD_Uninsulated Pipes and Acc
T3 | C50 | ARC_Plumbing Fixtures | HYD_Pipe Insulation | NL-C50-ARC_Plumbing Fixtures vs HYD_Pipe Insulation
T3 | C50 | ARC_Plumbing Fixtures | HYD_Uninsulated Hot and Cold Pipes and Acc | NL-C50-ARC_Plumbing Fixtures vs HYD_Uninsulated Hot and Cold Pipes and Acc
T3 | C50 | ARC_Plumbing Fixtures | HYD_Hot and Cold Insulation | NL-C50-ARC_Plumbing Fixtures vs HYD_Hot and Cold Insulation
T3 | C50 | ARC_Plumbing Fixtures | HYD_Plumbing Fixture | NL-C50-ARC_Plumbing Fixtures vs HYD_Plumbing Fixture
T3 | C50 | ARC_Plumbing Fixtures | MEC_Air Terminals | NL-C50-ARC_Plumbing Fixtures vs MEC_Air Terminals
T3 | C50 | ARC_Plumbing Fixtures | MEC_Uninsulated Duct and Acc | NL-C50-ARC_Plumbing Fixtures vs MEC_Uninsulated Duct and Acc
T3 | C50 | ARC_Plumbing Fixtures | MEC_Duct Insulation | NL-C50-ARC_Plumbing Fixtures vs MEC_Duct Insulation
T3 | C50 | ARC_Plumbing Fixtures | MEC_Pipe Insulation | NL-C50-ARC_Plumbing Fixtures vs MEC_Pipe Insulation
T3 | C50 | ARC_Plumbing Fixtures | MEC_Uninsulated Pipes and Acc | NL-C50-ARC_Plumbing Fixtures vs MEC_Uninsulated Pipes and Acc
T3 | C50 | ARC_Plumbing Fixtures | MEC_Uninulated Flexi duct | NL-C50-ARC_Plumbing Fixtures vs MEC_Uninulated Flexi duct
T3 | C50 | ARC_Plumbing Fixtures | MEC_Equipment | NL-C50-ARC_Plumbing Fixtures vs MEC_Equipment
T3 | C50 | ARC_Plumbing Fixtures | ELE_Cable Tray and Fittings | NL-C50-ARC_Plumbing Fixtures vs ELE_Cable Tray and Fittings
T3 | C50 | ARC_Plumbing Fixtures | ELE_Conduit* | NL-C50-ARC_Plumbing Fixtures vs ELE_Conduit*
T3 | C50 | ARC_Plumbing Fixtures | ELE_Electrical Equip. | NL-C50-ARC_Plumbing Fixtures vs ELE_Electrical Equip.
T3 | C50 | ARC_Plumbing Fixtures | ELE_Small Devices | NL-C50-ARC_Plumbing Fixtures vs ELE_Small Devices
T3 | C50 | ARC_Plumbing Fixtures | ELE_Services Lighting Fixtures | NL-C50-ARC_Plumbing Fixtures vs ELE_Services Lighting Fixtures
0 | 0 | ARC_Plumbing Fixtures | FIR_Fire Pipes | NL-0-ARC_Plumbing Fixtures vs FIR_Fire Pipes
0 | 0 | ARC_Plumbing Fixtures | FIR_Sprinklers Heads | NL-0-ARC_Plumbing Fixtures vs FIR_Sprinklers Heads
0 | 0 | ARC_Plumbing Fixtures | FIR_Heat or Smoke Detectors | NL-0-ARC_Plumbing Fixtures vs FIR_Heat or Smoke Detectors
0 | 0 | ARC_SOG Floor Insulation | ARC_SOG Floor Insulation | NL-0-ARC_SOG Floor Insulation vs ARC_SOG Floor Insulation
0 | 0 | ARC_SOG Floor Insulation | STR_Seismic Elements | NL-0-ARC_SOG Floor Insulation vs STR_Seismic Elements
0 | 0 | ARC_SOG Floor Insulation | STR_Conc work Excl Floor Slab | NL-0-ARC_SOG Floor Insulation vs STR_Conc work Excl Floor Slab
0 | 0 | ARC_SOG Floor Insulation | STR_Steelwork (Bracing and Columns) | NL-0-ARC_SOG Floor Insulation vs STR_Steelwork (Bracing and Columns)
0 | 0 | ARC_SOG Floor Insulation | STR Floor | NL-0-ARC_SOG Floor Insulation vs STR Floor
T1 | HC | ARC_SOG Floor Insulation | HYD_Uninsulated Pipes and Acc | NL-HC-ARC_SOG Floor Insulation vs HYD_Uninsulated Pipes and Acc
T1 | HC | ARC_SOG Floor Insulation | HYD_Pipe Insulation | NL-HC-ARC_SOG Floor Insulation vs HYD_Pipe Insulation
T1 | HC | ARC_SOG Floor Insulation | HYD_Uninsulated Hot and Cold Pipes and Acc | NL-HC-ARC_SOG Floor Insulation vs HYD_Uninsulated Hot and Cold Pipes and Acc
T1 | HC | ARC_SOG Floor Insulation | HYD_Hot and Cold Insulation | NL-HC-ARC_SOG Floor Insulation vs HYD_Hot and Cold Insulation
T1 | HC | ARC_SOG Floor Insulation | HYD_Plumbing Fixture | NL-HC-ARC_SOG Floor Insulation vs HYD_Plumbing Fixture
T1 | HC | ARC_SOG Floor Insulation | MEC_Air Terminals | NL-HC-ARC_SOG Floor Insulation vs MEC_Air Terminals
T1 | HC | ARC_SOG Floor Insulation | MEC_Uninsulated Duct and Acc | NL-HC-ARC_SOG Floor Insulation vs MEC_Uninsulated Duct and Acc
T1 | HC | ARC_SOG Floor Insulation | MEC_Duct Insulation | NL-HC-ARC_SOG Floor Insulation vs MEC_Duct Insulation
T1 | HC | ARC_SOG Floor Insulation | MEC_Pipe Insulation | NL-HC-ARC_SOG Floor Insulation vs MEC_Pipe Insulation
T1 | HC | ARC_SOG Floor Insulation | MEC_Uninsulated Pipes and Acc | NL-HC-ARC_SOG Floor Insulation vs MEC_Uninsulated Pipes and Acc
T1 | HC | ARC_SOG Floor Insulation | MEC_Uninulated Flexi duct | NL-HC-ARC_SOG Floor Insulation vs MEC_Uninulated Flexi duct
T1 | HC | ARC_SOG Floor Insulation | MEC_Equipment | NL-HC-ARC_SOG Floor Insulation vs MEC_Equipment
T1 | HC | ARC_SOG Floor Insulation | ELE_Cable Tray and Fittings | NL-HC-ARC_SOG Floor Insulation vs ELE_Cable Tray and Fittings
T1 | HC | ARC_SOG Floor Insulation | ELE_Conduit* | NL-HC-ARC_SOG Floor Insulation vs ELE_Conduit*
T1 | HC | ARC_SOG Floor Insulation | ELE_Electrical Equip. | NL-HC-ARC_SOG Floor Insulation vs ELE_Electrical Equip.
0 | 0 | ARC_SOG Floor Insulation | ELE_Small Devices | NL-0-ARC_SOG Floor Insulation vs ELE_Small Devices
0 | 0 | ARC_SOG Floor Insulation | ELE_Services Lighting Fixtures | NL-0-ARC_SOG Floor Insulation vs ELE_Services Lighting Fixtures
T1 | HC | ARC_SOG Floor Insulation | FIR_Fire Pipes | NL-HC-ARC_SOG Floor Insulation vs FIR_Fire Pipes
0 | 0 | ARC_SOG Floor Insulation | FIR_Sprinklers Heads | NL-0-ARC_SOG Floor Insulation vs FIR_Sprinklers Heads
0 | 0 | ARC_SOG Floor Insulation | FIR_Heat or Smoke Detectors | NL-0-ARC_SOG Floor Insulation vs FIR_Heat or Smoke Detectors
0 | 0 | STR_Seismic Elements | STR_Seismic Elements | NL-0-STR_Seismic Elements vs STR_Seismic Elements
T2 | C50 | STR_Seismic Elements | STR_Conc work Excl Floor Slab | NL-C50-STR_Seismic Elements vs STR_Conc work Excl Floor Slab
T2 | C50 | STR_Seismic Elements | STR_Steelwork (Bracing and Columns) | NL-C50-STR_Seismic Elements vs STR_Steelwork (Bracing and Columns)
T2 | C50 | STR_Seismic Elements | STR Floor | NL-C50-STR_Seismic Elements vs STR Floor
T2 | C50 | STR_Seismic Elements | HYD_Uninsulated Pipes and Acc | NL-C50-STR_Seismic Elements vs HYD_Uninsulated Pipes and Acc
T2 | C50 | STR_Seismic Elements | HYD_Pipe Insulation | NL-C50-STR_Seismic Elements vs HYD_Pipe Insulation
T2 | C50 | STR_Seismic Elements | HYD_Uninsulated Hot and Cold Pipes and Acc | NL-C50-STR_Seismic Elements vs HYD_Uninsulated Hot and Cold Pipes and Acc
T2 | C50 | STR_Seismic Elements | HYD_Hot and Cold Insulation | NL-C50-STR_Seismic Elements vs HYD_Hot and Cold Insulation
T2 | C50 | STR_Seismic Elements | HYD_Plumbing Fixture | NL-C50-STR_Seismic Elements vs HYD_Plumbing Fixture
T2 | C50 | STR_Seismic Elements | MEC_Air Terminals | NL-C50-STR_Seismic Elements vs MEC_Air Terminals
T2 | C50 | STR_Seismic Elements | MEC_Uninsulated Duct and Acc | NL-C50-STR_Seismic Elements vs MEC_Uninsulated Duct and Acc
T2 | C50 | STR_Seismic Elements | MEC_Duct Insulation | NL-C50-STR_Seismic Elements vs MEC_Duct Insulation
T2 | C50 | STR_Seismic Elements | MEC_Pipe Insulation | NL-C50-STR_Seismic Elements vs MEC_Pipe Insulation
T2 | C50 | STR_Seismic Elements | MEC_Uninsulated Pipes and Acc | NL-C50-STR_Seismic Elements vs MEC_Uninsulated Pipes and Acc
T2 | C50 | STR_Seismic Elements | MEC_Uninulated Flexi duct | NL-C50-STR_Seismic Elements vs MEC_Uninulated Flexi duct
T2 | C50 | STR_Seismic Elements | MEC_Equipment | NL-C50-STR_Seismic Elements vs MEC_Equipment
T2 | C50 | STR_Seismic Elements | ELE_Cable Tray and Fittings | NL-C50-STR_Seismic Elements vs ELE_Cable Tray and Fittings
T2 | C50 | STR_Seismic Elements | ELE_Conduit* | NL-C50-STR_Seismic Elements vs ELE_Conduit*
T2 | C50 | STR_Seismic Elements | ELE_Electrical Equip. | NL-C50-STR_Seismic Elements vs ELE_Electrical Equip.
T2 | C50 | STR_Seismic Elements | ELE_Small Devices | NL-C50-STR_Seismic Elements vs ELE_Small Devices
T2 | C50 | STR_Seismic Elements | ELE_Services Lighting Fixtures | NL-C50-STR_Seismic Elements vs ELE_Services Lighting Fixtures
T2 | C50 | STR_Seismic Elements | FIR_Fire Pipes | NL-C50-STR_Seismic Elements vs FIR_Fire Pipes
0 | 0 | STR_Seismic Elements | FIR_Sprinklers Heads | NL-0-STR_Seismic Elements vs FIR_Sprinklers Heads
0 | 0 | STR_Seismic Elements | FIR_Heat or Smoke Detectors | NL-0-STR_Seismic Elements vs FIR_Heat or Smoke Detectors
0 | 0 | STR_Conc work Excl Floor Slab | STR_Conc work Excl Floor Slab | NL-0-STR_Conc work Excl Floor Slab vs STR_Conc work Excl Floor Slab
0 | 0 | STR_Steelwork (Bracing and Columns) | STR_Steelwork (Bracing and Columns) | NL-0-STR_Steelwork (Bracing and Columns) vs STR_Steelwork (Bracing and Columns)
0 | 0 | STR_Conc work Excl Floor Slab | STR Floor | NL-0-STR_Conc work Excl Floor Slab vs STR Floor
T1 | C50 | STR_Conc work Excl Floor Slab | HYD_Uninsulated Pipes and Acc | NL-C50-STR_Conc work Excl Floor Slab vs HYD_Uninsulated Pipes and Acc
T1 | C50 | STR_Conc work Excl Floor Slab | HYD_Pipe Insulation | NL-C50-STR_Conc work Excl Floor Slab vs HYD_Pipe Insulation
T1 | C50 | STR_Conc work Excl Floor Slab | HYD_Uninsulated Hot and Cold Pipes and Acc | NL-C50-STR_Conc work Excl Floor Slab vs HYD_Uninsulated Hot and Cold Pipes and Acc
T1 | C50 | STR_Conc work Excl Floor Slab | HYD_Hot and Cold Insulation | NL-C50-STR_Conc work Excl Floor Slab vs HYD_Hot and Cold Insulation
T1 | C50 | STR_Conc work Excl Floor Slab | HYD_Plumbing Fixture | NL-C50-STR_Conc work Excl Floor Slab vs HYD_Plumbing Fixture
T1 | C50 | STR_Conc work Excl Floor Slab | MEC_Air Terminals | NL-C50-STR_Conc work Excl Floor Slab vs MEC_Air Terminals
T1 | C50 | STR_Conc work Excl Floor Slab | MEC_Uninsulated Duct and Acc | NL-C50-STR_Conc work Excl Floor Slab vs MEC_Uninsulated Duct and Acc
T1 | C50 | STR_Conc work Excl Floor Slab | MEC_Duct Insulation | NL-C50-STR_Conc work Excl Floor Slab vs MEC_Duct Insulation
T1 | C50 | STR_Conc work Excl Floor Slab | MEC_Pipe Insulation | NL-C50-STR_Conc work Excl Floor Slab vs MEC_Pipe Insulation
T1 | C50 | STR_Conc work Excl Floor Slab | MEC_Uninsulated Pipes and Acc | NL-C50-STR_Conc work Excl Floor Slab vs MEC_Uninsulated Pipes and Acc
T1 | C50 | STR_Conc work Excl Floor Slab | MEC_Uninulated Flexi duct | NL-C50-STR_Conc work Excl Floor Slab vs MEC_Uninulated Flexi duct
T1 | C50 | STR_Conc work Excl Floor Slab | MEC_Equipment | NL-C50-STR_Conc work Excl Floor Slab vs MEC_Equipment
T1 | C50 | STR_Conc work Excl Floor Slab | ELE_Cable Tray and Fittings | NL-C50-STR_Conc work Excl Floor Slab vs ELE_Cable Tray and Fittings
T1 | C50 | STR_Conc work Excl Floor Slab | ELE_Conduit* | NL-C50-STR_Conc work Excl Floor Slab vs ELE_Conduit*
T1 | C50 | STR_Conc work Excl Floor Slab | ELE_Electrical Equip. | NL-C50-STR_Conc work Excl Floor Slab vs ELE_Electrical Equip.
T1 | C50 | STR_Conc work Excl Floor Slab | ELE_Small Devices | NL-C50-STR_Conc work Excl Floor Slab vs ELE_Small Devices
T1 | C50 | STR_Conc work Excl Floor Slab | ELE_Services Lighting Fixtures | NL-C50-STR_Conc work Excl Floor Slab vs ELE_Services Lighting Fixtures
T1 | C50 | STR_Conc work Excl Floor Slab | FIR_Fire Pipes | NL-C50-STR_Conc work Excl Floor Slab vs FIR_Fire Pipes
0 | 0 | STR_Conc work Excl Floor Slab | FIR_Sprinklers Heads | NL-0-STR_Conc work Excl Floor Slab vs FIR_Sprinklers Heads
0 | 0 | STR_Conc work Excl Floor Slab | FIR_Heat or Smoke Detectors | NL-0-STR_Conc work Excl Floor Slab vs FIR_Heat or Smoke Detectors
0 | 0 | STR_Steelwork (Bracing and Columns) | STR_Steelwork (Bracing and Columns) | NL-0-STR_Steelwork (Bracing and Columns) vs STR_Steelwork (Bracing and Columns)
0 | 0 | STR_Steelwork (Bracing and Columns) | STR Floor | NL-0-STR_Steelwork (Bracing and Columns) vs STR Floor
T1 | C50 | STR_Steelwork (Bracing and Columns) | HYD_Uninsulated Pipes and Acc | NL-C50-STR_Steelwork (Bracing and Columns) vs HYD_Uninsulated Pipes and Acc
T1 | C50 | STR_Steelwork (Bracing and Columns) | HYD_Pipe Insulation | NL-C50-STR_Steelwork (Bracing and Columns) vs HYD_Pipe Insulation
T1 | C50 | STR_Steelwork (Bracing and Columns) | HYD_Uninsulated Hot and Cold Pipes and Acc | NL-C50-STR_Steelwork (Bracing and Columns) vs HYD_Uninsulated Hot and Cold Pipes and Acc
T1 | C50 | STR_Steelwork (Bracing and Columns) | HYD_Hot and Cold Insulation | NL-C50-STR_Steelwork (Bracing and Columns) vs HYD_Hot and Cold Insulation
0 | 0 | STR_Steelwork (Bracing and Columns) | HYD_Plumbing Fixture | NL-0-STR_Steelwork (Bracing and Columns) vs HYD_Plumbing Fixture
T1 | C50 | STR_Steelwork (Bracing and Columns) | MEC_Air Terminals | NL-C50-STR_Steelwork (Bracing and Columns) vs MEC_Air Terminals
T1 | C50 | STR_Steelwork (Bracing and Columns) | MEC_Uninsulated Duct and Acc | NL-C50-STR_Steelwork (Bracing and Columns) vs MEC_Uninsulated Duct and Acc
T1 | C50 | STR_Steelwork (Bracing and Columns) | MEC_Duct Insulation | NL-C50-STR_Steelwork (Bracing and Columns) vs MEC_Duct Insulation
T1 | C50 | STR_Steelwork (Bracing and Columns) | MEC_Pipe Insulation | NL-C50-STR_Steelwork (Bracing and Columns) vs MEC_Pipe Insulation
T1 | C50 | STR_Steelwork (Bracing and Columns) | MEC_Uninsulated Pipes and Acc | NL-C50-STR_Steelwork (Bracing and Columns) vs MEC_Uninsulated Pipes and Acc
T1 | C50 | STR_Steelwork (Bracing and Columns) | MEC_Uninulated Flexi duct | NL-C50-STR_Steelwork (Bracing and Columns) vs MEC_Uninulated Flexi duct
T1 | C50 | STR_Steelwork (Bracing and Columns) | MEC_Equipment | NL-C50-STR_Steelwork (Bracing and Columns) vs MEC_Equipment
T1 | C50 | STR_Steelwork (Bracing and Columns) | ELE_Cable Tray and Fittings | NL-C50-STR_Steelwork (Bracing and Columns) vs ELE_Cable Tray and Fittings
T1 | C50 | STR_Steelwork (Bracing and Columns) | ELE_Conduit* | NL-C50-STR_Steelwork (Bracing and Columns) vs ELE_Conduit*
T1 | C50 | STR_Steelwork (Bracing and Columns) | ELE_Electrical Equip. | NL-C50-STR_Steelwork (Bracing and Columns) vs ELE_Electrical Equip.
T1 | C50 | STR_Steelwork (Bracing and Columns) | ELE_Small Devices | NL-C50-STR_Steelwork (Bracing and Columns) vs ELE_Small Devices
T1 | C50 | STR_Steelwork (Bracing and Columns) | ELE_Services Lighting Fixtures | NL-C50-STR_Steelwork (Bracing and Columns) vs ELE_Services Lighting Fixtures
0 | 0 | STR_Steelwork (Bracing and Columns) | FIR_Fire Pipes | NL-0-STR_Steelwork (Bracing and Columns) vs FIR_Fire Pipes
0 | 0 | STR_Steelwork (Bracing and Columns) | FIR_Sprinklers Heads | NL-0-STR_Steelwork (Bracing and Columns) vs FIR_Sprinklers Heads
0 | 0 | STR_Steelwork (Bracing and Columns) | FIR_Heat or Smoke Detectors | NL-0-STR_Steelwork (Bracing and Columns) vs FIR_Heat or Smoke Detectors
0 | 0 | STR Floor | STR Floor | NL-0-STR Floor vs STR Floor
T1 | C50 | STR Floor | HYD_Uninsulated Pipes and Acc | NL-C50-STR Floor vs HYD_Uninsulated Pipes and Acc
T1 | C50 | STR Floor | HYD_Pipe Insulation | NL-C50-STR Floor vs HYD_Pipe Insulation
T1 | C50 | STR Floor | HYD_Uninsulated Hot and Cold Pipes and Acc | NL-C50-STR Floor vs HYD_Uninsulated Hot and Cold Pipes and Acc
T1 | C50 | STR Floor | HYD_Hot and Cold Insulation | NL-C50-STR Floor vs HYD_Hot and Cold Insulation
0 | 0 | STR Floor | HYD_Plumbing Fixture | NL-0-STR Floor vs HYD_Plumbing Fixture
T1 | C50 | STR Floor | MEC_Air Terminals | NL-C50-STR Floor vs MEC_Air Terminals
T1 | C50 | STR Floor | MEC_Uninsulated Duct and Acc | NL-C50-STR Floor vs MEC_Uninsulated Duct and Acc
T1 | C50 | STR Floor | MEC_Duct Insulation | NL-C50-STR Floor vs MEC_Duct Insulation
T1 | C50 | STR Floor | MEC_Pipe Insulation | NL-C50-STR Floor vs MEC_Pipe Insulation
T1 | C50 | STR Floor | MEC_Uninsulated Pipes and Acc | NL-C50-STR Floor vs MEC_Uninsulated Pipes and Acc
T1 | C50 | STR Floor | MEC_Uninulated Flexi duct | NL-C50-STR Floor vs MEC_Uninulated Flexi duct
T1 | C50 | STR Floor | MEC_Equipment | NL-C50-STR Floor vs MEC_Equipment
T1 | C50 | STR Floor | ELE_Cable Tray and Fittings | NL-C50-STR Floor vs ELE_Cable Tray and Fittings
T1 | C50 | STR Floor | ELE_Conduit* | NL-C50-STR Floor vs ELE_Conduit*
T1 | C50 | STR Floor | ELE_Electrical Equip. | NL-C50-STR Floor vs ELE_Electrical Equip.
T1 | C50 | STR Floor | ELE_Small Devices | NL-C50-STR Floor vs ELE_Small Devices
T1 | C50 | STR Floor | ELE_Services Lighting Fixtures | NL-C50-STR Floor vs ELE_Services Lighting Fixtures
T1 | C50 | STR Floor | FIR_Fire Pipes | NL-C50-STR Floor vs FIR_Fire Pipes
0 | 0 | STR Floor | FIR_Sprinklers Heads | NL-0-STR Floor vs FIR_Sprinklers Heads
0 | 0 | STR Floor | FIR_Heat or Smoke Detectors | NL-0-STR Floor vs FIR_Heat or Smoke Detectors
0 | 0 | HYD_Uninsulated Pipes | HYD_Uninsulated Pipes and Acc | NL-0-HYD_Uninsulated Pipes vs HYD_Uninsulated Pipes and Acc
T2 | C50 | HYD_Uninsulated Pipes | HYD_Pipe Insulation | NL-C50-HYD_Uninsulated Pipes vs HYD_Pipe Insulation
T2 | C50 | HYD_Uninsulated Pipes | HYD_Uninsulated Hot and Cold Pipes and Acc | NL-C50-HYD_Uninsulated Pipes vs HYD_Uninsulated Hot and Cold Pipes and Acc
T2 | C50 | HYD_Uninsulated Pipes | HYD_Hot and Cold Insulation | NL-C50-HYD_Uninsulated Pipes vs HYD_Hot and Cold Insulation
T2 | C50 | HYD_Uninsulated Pipes | HYD_Plumbing Fixture | NL-C50-HYD_Uninsulated Pipes vs HYD_Plumbing Fixture
T2 | C50 | HYD_Uninsulated Pipes | MEC_Air Terminals | NL-C50-HYD_Uninsulated Pipes vs MEC_Air Terminals
T2 | C50 | HYD_Uninsulated Pipes | MEC_Uninsulated Duct and Acc | NL-C50-HYD_Uninsulated Pipes vs MEC_Uninsulated Duct and Acc
T2 | C50 | HYD_Uninsulated Pipes | MEC_Duct Insulation | NL-C50-HYD_Uninsulated Pipes vs MEC_Duct Insulation
T2 | C50 | HYD_Uninsulated Pipes | MEC_Pipe Insulation | NL-C50-HYD_Uninsulated Pipes vs MEC_Pipe Insulation
T2 | C50 | HYD_Uninsulated Pipes | MEC_Uninsulated Pipes and Acc | NL-C50-HYD_Uninsulated Pipes vs MEC_Uninsulated Pipes and Acc
T2 | C50 | HYD_Uninsulated Pipes | MEC_Uninulated Flexi duct | NL-C50-HYD_Uninsulated Pipes vs MEC_Uninulated Flexi duct
T2 | C50 | HYD_Uninsulated Pipes | MEC_Equipment | NL-C50-HYD_Uninsulated Pipes vs MEC_Equipment
T2 | C50 | HYD_Uninsulated Pipes | ELE_Cable Tray and Fittings | NL-C50-HYD_Uninsulated Pipes vs ELE_Cable Tray and Fittings
T2 | C50 | HYD_Uninsulated Pipes | ELE_Conduit* | NL-C50-HYD_Uninsulated Pipes vs ELE_Conduit*
T2 | C50 | HYD_Uninsulated Pipes | ELE_Electrical Equip. | NL-C50-HYD_Uninsulated Pipes vs ELE_Electrical Equip.
T2 | C50 | HYD_Uninsulated Pipes | ELE_Small Devices | NL-C50-HYD_Uninsulated Pipes vs ELE_Small Devices
T2 | C50 | HYD_Uninsulated Pipes | ELE_Services Lighting Fixtures | NL-C50-HYD_Uninsulated Pipes vs ELE_Services Lighting Fixtures
T2 | C50 | HYD_Uninsulated Pipes | FIR_Fire Pipes | NL-C50-HYD_Uninsulated Pipes vs FIR_Fire Pipes
T2 | C50 | HYD_Uninsulated Pipes | FIR_Sprinklers Heads | NL-C50-HYD_Uninsulated Pipes vs FIR_Sprinklers Heads
T2 | C50 | HYD_Uninsulated Pipes | FIR_Heat or Smoke Detectors | NL-C50-HYD_Uninsulated Pipes vs FIR_Heat or Smoke Detectors
0 | 0 | HYD_Pipe Insulation | HYD_Pipe Insulation | NL-0-HYD_Pipe Insulation vs HYD_Pipe Insulation
T2 | C50 | HYD_Pipe Insulation | HYD_Uninsulated Hot and Cold Pipes and Acc | NL-C50-HYD_Pipe Insulation vs HYD_Uninsulated Hot and Cold Pipes and Acc
T2 | C50 | HYD_Pipe Insulation | HYD_Hot and Cold Insulation | NL-C50-HYD_Pipe Insulation vs HYD_Hot and Cold Insulation
T2 | C50 | HYD_Pipe Insulation | HYD_Plumbing Fixture | NL-C50-HYD_Pipe Insulation vs HYD_Plumbing Fixture
T2 | C50 | HYD_Pipe Insulation | MEC_Air Terminals | NL-C50-HYD_Pipe Insulation vs MEC_Air Terminals
T2 | C50 | HYD_Pipe Insulation | MEC_Uninsulated Duct and Acc | NL-C50-HYD_Pipe Insulation vs MEC_Uninsulated Duct and Acc
T2 | C50 | HYD_Pipe Insulation | MEC_Duct Insulation | NL-C50-HYD_Pipe Insulation vs MEC_Duct Insulation
T2 | C50 | HYD_Pipe Insulation | MEC_Pipe Insulation | NL-C50-HYD_Pipe Insulation vs MEC_Pipe Insulation
T2 | C50 | HYD_Pipe Insulation | MEC_Uninsulated Pipes and Acc | NL-C50-HYD_Pipe Insulation vs MEC_Uninsulated Pipes and Acc
T2 | C50 | HYD_Pipe Insulation | MEC_Uninulated Flexi duct | NL-C50-HYD_Pipe Insulation vs MEC_Uninulated Flexi duct
T2 | C50 | HYD_Pipe Insulation | MEC_Equipment | NL-C50-HYD_Pipe Insulation vs MEC_Equipment
T2 | C50 | HYD_Pipe Insulation | ELE_Cable Tray and Fittings | NL-C50-HYD_Pipe Insulation vs ELE_Cable Tray and Fittings
T2 | C50 | HYD_Pipe Insulation | ELE_Conduit* | NL-C50-HYD_Pipe Insulation vs ELE_Conduit*
T2 | C50 | HYD_Pipe Insulation | ELE_Electrical Equip. | NL-C50-HYD_Pipe Insulation vs ELE_Electrical Equip.
T2 | C50 | HYD_Pipe Insulation | ELE_Small Devices | NL-C50-HYD_Pipe Insulation vs ELE_Small Devices
T2 | C50 | HYD_Pipe Insulation | ELE_Services Lighting Fixtures | NL-C50-HYD_Pipe Insulation vs ELE_Services Lighting Fixtures
T2 | C50 | HYD_Pipe Insulation | FIR_Fire Pipes | NL-C50-HYD_Pipe Insulation vs FIR_Fire Pipes
T2 | C50 | HYD_Pipe Insulation | FIR_Sprinklers Heads | NL-C50-HYD_Pipe Insulation vs FIR_Sprinklers Heads
T2 | C50 | HYD_Pipe Insulation | FIR_Heat or Smoke Detectors | NL-C50-HYD_Pipe Insulation vs FIR_Heat or Smoke Detectors
0 | 0 | HYD_Uninsulated Hot and Cold Pipes and Acc | HYD_Uninsulated Hot and Cold Pipes and Acc | NL-0-HYD_Uninsulated Hot and Cold Pipes and Acc vs HYD_Uninsulated Hot and Cold Pipes and Acc
T2 | C50 | HYD_Uninsulated Hot and Cold Pipes and Acc | HYD_Hot and Cold Insulation | NL-C50-HYD_Uninsulated Hot and Cold Pipes and Acc vs HYD_Hot and Cold Insulation
T2 | C50 | HYD_Uninsulated Hot and Cold Pipes and Acc | HYD_Plumbing Fixture | NL-C50-HYD_Uninsulated Hot and Cold Pipes and Acc vs HYD_Plumbing Fixture
T2 | C50 | HYD_Uninsulated Hot and Cold Pipes and Acc | MEC_Air Terminals | NL-C50-HYD_Uninsulated Hot and Cold Pipes and Acc vs MEC_Air Terminals
T2 | C50 | HYD_Uninsulated Hot and Cold Pipes and Acc | MEC_Uninsulated Duct and Acc | NL-C50-HYD_Uninsulated Hot and Cold Pipes and Acc vs MEC_Uninsulated Duct and Acc
T2 | C50 | HYD_Uninsulated Hot and Cold Pipes and Acc | MEC_Duct Insulation | NL-C50-HYD_Uninsulated Hot and Cold Pipes and Acc vs MEC_Duct Insulation
T2 | C50 | HYD_Uninsulated Hot and Cold Pipes and Acc | MEC_Pipe Insulation | NL-C50-HYD_Uninsulated Hot and Cold Pipes and Acc vs MEC_Pipe Insulation
T2 | C50 | HYD_Uninsulated Hot and Cold Pipes and Acc | MEC_Uninsulated Pipes and Acc | NL-C50-HYD_Uninsulated Hot and Cold Pipes and Acc vs MEC_Uninsulated Pipes and Acc
T2 | C50 | HYD_Uninsulated Hot and Cold Pipes and Acc | MEC_Uninulated Flexi duct | NL-C50-HYD_Uninsulated Hot and Cold Pipes and Acc vs MEC_Uninulated Flexi duct
T2 | C50 | HYD_Uninsulated Hot and Cold Pipes and Acc | MEC_Equipment | NL-C50-HYD_Uninsulated Hot and Cold Pipes and Acc vs MEC_Equipment
T2 | C50 | HYD_Uninsulated Hot and Cold Pipes and Acc | ELE_Cable Tray and Fittings | NL-C50-HYD_Uninsulated Hot and Cold Pipes and Acc vs ELE_Cable Tray and Fittings
T2 | C50 | HYD_Uninsulated Hot and Cold Pipes and Acc | ELE_Conduit* | NL-C50-HYD_Uninsulated Hot and Cold Pipes and Acc vs ELE_Conduit*
T2 | C50 | HYD_Uninsulated Hot and Cold Pipes and Acc | ELE_Electrical Equip. | NL-C50-HYD_Uninsulated Hot and Cold Pipes and Acc vs ELE_Electrical Equip.
T2 | C50 | HYD_Uninsulated Hot and Cold Pipes and Acc | ELE_Small Devices | NL-C50-HYD_Uninsulated Hot and Cold Pipes and Acc vs ELE_Small Devices
T2 | C50 | HYD_Uninsulated Hot and Cold Pipes and Acc | ELE_Services Lighting Fixtures | NL-C50-HYD_Uninsulated Hot and Cold Pipes and Acc vs ELE_Services Lighting Fixtures
T2 | C50 | HYD_Uninsulated Hot and Cold Pipes and Acc | FIR_Fire Pipes | NL-C50-HYD_Uninsulated Hot and Cold Pipes and Acc vs FIR_Fire Pipes
T2 | C50 | HYD_Uninsulated Hot and Cold Pipes and Acc | FIR_Sprinklers Heads | NL-C50-HYD_Uninsulated Hot and Cold Pipes and Acc vs FIR_Sprinklers Heads
T2 | C50 | HYD_Uninsulated Hot and Cold Pipes and Acc | FIR_Heat or Smoke Detectors | NL-C50-HYD_Uninsulated Hot and Cold Pipes and Acc vs FIR_Heat or Smoke Detectors
0 | 0 | HYD_Hot and Cold Insulation | HYD_Hot and Cold Insulation | NL-0-HYD_Hot and Cold Insulation vs HYD_Hot and Cold Insulation
T2 | C50 | HYD_Hot and Cold Insulation | HYD_Plumbing Fixture | NL-C50-HYD_Hot and Cold Insulation vs HYD_Plumbing Fixture
T2 | C50 | HYD_Hot and Cold Insulation | MEC_Air Terminals | NL-C50-HYD_Hot and Cold Insulation vs MEC_Air Terminals
T2 | C50 | HYD_Hot and Cold Insulation | MEC_Uninsulated Duct and Acc | NL-C50-HYD_Hot and Cold Insulation vs MEC_Uninsulated Duct and Acc
T2 | C50 | HYD_Hot and Cold Insulation | MEC_Duct Insulation | NL-C50-HYD_Hot and Cold Insulation vs MEC_Duct Insulation
T2 | C50 | HYD_Hot and Cold Insulation | MEC_Pipe Insulation | NL-C50-HYD_Hot and Cold Insulation vs MEC_Pipe Insulation
T2 | C50 | HYD_Hot and Cold Insulation | MEC_Uninsulated Pipes and Acc | NL-C50-HYD_Hot and Cold Insulation vs MEC_Uninsulated Pipes and Acc
T2 | C50 | HYD_Hot and Cold Insulation | MEC_Uninulated Flexi duct | NL-C50-HYD_Hot and Cold Insulation vs MEC_Uninulated Flexi duct
T2 | C50 | HYD_Hot and Cold Insulation | MEC_Equipment | NL-C50-HYD_Hot and Cold Insulation vs MEC_Equipment
T2 | C50 | HYD_Hot and Cold Insulation | ELE_Cable Tray and Fittings | NL-C50-HYD_Hot and Cold Insulation vs ELE_Cable Tray and Fittings
T2 | C50 | HYD_Hot and Cold Insulation | ELE_Conduit* | NL-C50-HYD_Hot and Cold Insulation vs ELE_Conduit*
T2 | C50 | HYD_Hot and Cold Insulation | ELE_Electrical Equip. | NL-C50-HYD_Hot and Cold Insulation vs ELE_Electrical Equip.
T2 | C50 | HYD_Hot and Cold Insulation | ELE_Small Devices | NL-C50-HYD_Hot and Cold Insulation vs ELE_Small Devices
T2 | C50 | HYD_Hot and Cold Insulation | ELE_Services Lighting Fixtures | NL-C50-HYD_Hot and Cold Insulation vs ELE_Services Lighting Fixtures
T2 | C50 | HYD_Hot and Cold Insulation | FIR_Fire Pipes | NL-C50-HYD_Hot and Cold Insulation vs FIR_Fire Pipes
T2 | C50 | HYD_Hot and Cold Insulation | FIR_Sprinklers Heads | NL-C50-HYD_Hot and Cold Insulation vs FIR_Sprinklers Heads
T2 | C50 | HYD_Hot and Cold Insulation | FIR_Heat or Smoke Detectors | NL-C50-HYD_Hot and Cold Insulation vs FIR_Heat or Smoke Detectors
0 | 0 | HYD_ Plumbing Fixture | HYD_Plumbing Fixture | NL-0-HYD_ Plumbing Fixture vs HYD_Plumbing Fixture
T2 | C50 | HYD_ Plumbing Fixture | MEC_Air Terminals | NL-C50-HYD_ Plumbing Fixture vs MEC_Air Terminals
T2 | C50 | HYD_ Plumbing Fixture | MEC_Uninsulated Duct and Acc | NL-C50-HYD_ Plumbing Fixture vs MEC_Uninsulated Duct and Acc
T2 | C50 | HYD_ Plumbing Fixture | MEC_Duct Insulation | NL-C50-HYD_ Plumbing Fixture vs MEC_Duct Insulation
T2 | C50 | HYD_ Plumbing Fixture | MEC_Pipe Insulation | NL-C50-HYD_ Plumbing Fixture vs MEC_Pipe Insulation
T2 | C50 | HYD_ Plumbing Fixture | MEC_Uninsulated Pipes and Acc | NL-C50-HYD_ Plumbing Fixture vs MEC_Uninsulated Pipes and Acc
T2 | C50 | HYD_ Plumbing Fixture | MEC_Uninulated Flexi duct | NL-C50-HYD_ Plumbing Fixture vs MEC_Uninulated Flexi duct
T2 | C50 | HYD_ Plumbing Fixture | MEC_Equipment | NL-C50-HYD_ Plumbing Fixture vs MEC_Equipment
T2 | C50 | HYD_ Plumbing Fixture | ELE_Cable Tray and Fittings | NL-C50-HYD_ Plumbing Fixture vs ELE_Cable Tray and Fittings
T2 | C50 | HYD_ Plumbing Fixture | ELE_Conduit* | NL-C50-HYD_ Plumbing Fixture vs ELE_Conduit*
T2 | C50 | HYD_ Plumbing Fixture | ELE_Electrical Equip. | NL-C50-HYD_ Plumbing Fixture vs ELE_Electrical Equip.
T2 | C50 | HYD_ Plumbing Fixture | ELE_Small Devices | NL-C50-HYD_ Plumbing Fixture vs ELE_Small Devices
T2 | C50 | HYD_ Plumbing Fixture | ELE_Services Lighting Fixtures | NL-C50-HYD_ Plumbing Fixture vs ELE_Services Lighting Fixtures
T2 | C50 | HYD_ Plumbing Fixture | FIR_Fire Pipes | NL-C50-HYD_ Plumbing Fixture vs FIR_Fire Pipes
T2 | C50 | HYD_ Plumbing Fixture | FIR_Sprinklers Heads | NL-C50-HYD_ Plumbing Fixture vs FIR_Sprinklers Heads
T2 | C50 | HYD_ Plumbing Fixture | FIR_Heat or Smoke Detectors | NL-C50-HYD_ Plumbing Fixture vs FIR_Heat or Smoke Detectors
0 | 0 | MEC_Air Terminals | MEC_Air Terminals | NL-0-MEC_Air Terminals vs MEC_Air Terminals
T2 | C50 | MEC_Air Terminals | MEC_Uninsulated Duct and Acc | NL-C50-MEC_Air Terminals vs MEC_Uninsulated Duct and Acc
T2 | C50 | MEC_Air Terminals | MEC_Duct Insulation | NL-C50-MEC_Air Terminals vs MEC_Duct Insulation
T2 | C50 | MEC_Air Terminals | MEC_Pipe Insulation | NL-C50-MEC_Air Terminals vs MEC_Pipe Insulation
T2 | C50 | MEC_Air Terminals | MEC_Uninsulated Pipes and Acc | NL-C50-MEC_Air Terminals vs MEC_Uninsulated Pipes and Acc
T2 | C50 | MEC_Air Terminals | MEC_Uninulated Flexi duct | NL-C50-MEC_Air Terminals vs MEC_Uninulated Flexi duct
T2 | C50 | MEC_Air Terminals | MEC_Equipment | NL-C50-MEC_Air Terminals vs MEC_Equipment
T2 | C50 | MEC_Air Terminals | ELE_Cable Tray and Fittings | NL-C50-MEC_Air Terminals vs ELE_Cable Tray and Fittings
T2 | C50 | MEC_Air Terminals | ELE_Conduit* | NL-C50-MEC_Air Terminals vs ELE_Conduit*
T2 | C50 | MEC_Air Terminals | ELE_Electrical Equip. | NL-C50-MEC_Air Terminals vs ELE_Electrical Equip.
T2 | C50 | MEC_Air Terminals | ELE_Small Devices | NL-C50-MEC_Air Terminals vs ELE_Small Devices
T2 | C50 | MEC_Air Terminals | ELE_Services Lighting Fixtures | NL-C50-MEC_Air Terminals vs ELE_Services Lighting Fixtures
T2 | C50 | MEC_Air Terminals | FIR_Fire Pipes | NL-C50-MEC_Air Terminals vs FIR_Fire Pipes
T2 | C50 | MEC_Air Terminals | FIR_Sprinklers Heads | NL-C50-MEC_Air Terminals vs FIR_Sprinklers Heads
T2 | C1500 | MEC_Air Terminals | FIR_Heat or Smoke Detectors | NL-C1500-MEC_Air Terminals vs FIR_Heat or Smoke Detectors
0 | 0 | MEC_Uninsulated Duct and Acc | MEC_Uninsulated Duct and Acc | NL-0-MEC_Uninsulated Duct and Acc vs MEC_Uninsulated Duct and Acc
T2 | C50 | MEC_Uninsulated Duct and Acc | MEC_Duct Insulation | NL-C50-MEC_Uninsulated Duct and Acc vs MEC_Duct Insulation
T2 | C50 | MEC_Uninsulated Duct and Acc | MEC_Pipe Insulation | NL-C50-MEC_Uninsulated Duct and Acc vs MEC_Pipe Insulation
T2 | C50 | MEC_Uninsulated Duct and Acc | MEC_Uninsulated Pipes and Acc | NL-C50-MEC_Uninsulated Duct and Acc vs MEC_Uninsulated Pipes and Acc
T2 | C50 | MEC_Uninsulated Duct and Acc | MEC_Uninulated Flexi duct | NL-C50-MEC_Uninsulated Duct and Acc vs MEC_Uninulated Flexi duct
T2 | C50 | MEC_Uninsulated Duct and Acc | MEC_Equipment | NL-C50-MEC_Uninsulated Duct and Acc vs MEC_Equipment
T2 | C50 | MEC_Uninsulated Duct and Acc | ELE_Cable Tray and Fittings | NL-C50-MEC_Uninsulated Duct and Acc vs ELE_Cable Tray and Fittings
T2 | C50 | MEC_Uninsulated Duct and Acc | ELE_Conduit* | NL-C50-MEC_Uninsulated Duct and Acc vs ELE_Conduit*
T2 | C50 | MEC_Uninsulated Duct and Acc | ELE_Electrical Equip. | NL-C50-MEC_Uninsulated Duct and Acc vs ELE_Electrical Equip.
T2 | C50 | MEC_Uninsulated Duct and Acc | ELE_Small Devices | NL-C50-MEC_Uninsulated Duct and Acc vs ELE_Small Devices
T2 | C50 | MEC_Uninsulated Duct and Acc | ELE_Services Lighting Fixtures | NL-C50-MEC_Uninsulated Duct and Acc vs ELE_Services Lighting Fixtures
T2 | C50 | MEC_Uninsulated Duct and Acc | FIR_Fire Pipes | NL-C50-MEC_Uninsulated Duct and Acc vs FIR_Fire Pipes
T2 | C50 | MEC_Uninsulated Duct and Acc | FIR_Sprinklers Heads | NL-C50-MEC_Uninsulated Duct and Acc vs FIR_Sprinklers Heads
T2 | C50 | MEC_Uninsulated Duct and Acc | FIR_Heat or Smoke Detectors | NL-C50-MEC_Uninsulated Duct and Acc vs FIR_Heat or Smoke Detectors
0 | 0 | MEC_Duct Insulation | MEC_Duct Insulation | NL-0-MEC_Duct Insulation vs MEC_Duct Insulation
T2 | C50 | MEC_Duct Insulation | MEC_Pipe Insulation | NL-C50-MEC_Duct Insulation vs MEC_Pipe Insulation
T2 | C50 | MEC_Duct Insulation | MEC_Uninsulated Pipes and Acc | NL-C50-MEC_Duct Insulation vs MEC_Uninsulated Pipes and Acc
T2 | C50 | MEC_Duct Insulation | MEC_Uninulated Flexi duct | NL-C50-MEC_Duct Insulation vs MEC_Uninulated Flexi duct
T2 | C50 | MEC_Duct Insulation | MEC_Equipment | NL-C50-MEC_Duct Insulation vs MEC_Equipment
T2 | C50 | MEC_Duct Insulation | ELE_Cable Tray and Fittings | NL-C50-MEC_Duct Insulation vs ELE_Cable Tray and Fittings
T2 | C50 | MEC_Duct Insulation | ELE_Conduit* | NL-C50-MEC_Duct Insulation vs ELE_Conduit*
T2 | C50 | MEC_Duct Insulation | ELE_Electrical Equip. | NL-C50-MEC_Duct Insulation vs ELE_Electrical Equip.
T2 | C50 | MEC_Duct Insulation | ELE_Small Devices | NL-C50-MEC_Duct Insulation vs ELE_Small Devices
T2 | C50 | MEC_Duct Insulation | ELE_Services Lighting Fixtures | NL-C50-MEC_Duct Insulation vs ELE_Services Lighting Fixtures
T2 | C50 | MEC_Duct Insulation | FIR_Fire Pipes | NL-C50-MEC_Duct Insulation vs FIR_Fire Pipes
T2 | C50 | MEC_Duct Insulation | FIR_Sprinklers Heads | NL-C50-MEC_Duct Insulation vs FIR_Sprinklers Heads
T2 | C50 | MEC_Duct Insulation | FIR_Heat or Smoke Detectors | NL-C50-MEC_Duct Insulation vs FIR_Heat or Smoke Detectors
0 | 0 | MEC_Pipe Insulation | MEC_Pipe Insulation | NL-0-MEC_Pipe Insulation vs MEC_Pipe Insulation
T2 | C50 | MEC_Pipe Insulation | MEC_Uninsulated Pipes and Acc | NL-C50-MEC_Pipe Insulation vs MEC_Uninsulated Pipes and Acc
T2 | C50 | MEC_Pipe Insulation | MEC_Uninulated Flexi duct | NL-C50-MEC_Pipe Insulation vs MEC_Uninulated Flexi duct
T2 | C50 | MEC_Pipe Insulation | MEC_Equipment | NL-C50-MEC_Pipe Insulation vs MEC_Equipment
T2 | C50 | MEC_Pipe Insulation | ELE_Cable Tray and Fittings | NL-C50-MEC_Pipe Insulation vs ELE_Cable Tray and Fittings
T2 | C50 | MEC_Pipe Insulation | ELE_Conduit* | NL-C50-MEC_Pipe Insulation vs ELE_Conduit*
T2 | C50 | MEC_Pipe Insulation | ELE_Electrical Equip. | NL-C50-MEC_Pipe Insulation vs ELE_Electrical Equip.
T2 | C50 | MEC_Pipe Insulation | ELE_Small Devices | NL-C50-MEC_Pipe Insulation vs ELE_Small Devices
T2 | C50 | MEC_Pipe Insulation | ELE_Services Lighting Fixtures | NL-C50-MEC_Pipe Insulation vs ELE_Services Lighting Fixtures
T2 | C50 | MEC_Pipe Insulation | FIR_Fire Pipes | NL-C50-MEC_Pipe Insulation vs FIR_Fire Pipes
T2 | C50 | MEC_Pipe Insulation | FIR_Sprinklers Heads | NL-C50-MEC_Pipe Insulation vs FIR_Sprinklers Heads
T2 | C50 | MEC_Pipe Insulation | FIR_Heat or Smoke Detectors | NL-C50-MEC_Pipe Insulation vs FIR_Heat or Smoke Detectors
0 | 0 | MEC_Uninsulated Pipes and Acc | MEC_Uninsulated Pipes and Acc | NL-0-MEC_Uninsulated Pipes and Acc vs MEC_Uninsulated Pipes and Acc
T2 | C50 | MEC_Uninsulated Pipes and Acc | MEC_Uninulated Flexi duct | NL-C50-MEC_Uninsulated Pipes and Acc vs MEC_Uninulated Flexi duct
T2 | C50 | MEC_Uninsulated Pipes and Acc | MEC_Equipment | NL-C50-MEC_Uninsulated Pipes and Acc vs MEC_Equipment
T2 | C50 | MEC_Uninsulated Pipes and Acc | ELE_Cable Tray and Fittings | NL-C50-MEC_Uninsulated Pipes and Acc vs ELE_Cable Tray and Fittings
T2 | C50 | MEC_Uninsulated Pipes and Acc | ELE_Conduit* | NL-C50-MEC_Uninsulated Pipes and Acc vs ELE_Conduit*
T2 | C50 | MEC_Uninsulated Pipes and Acc | ELE_Electrical Equip. | NL-C50-MEC_Uninsulated Pipes and Acc vs ELE_Electrical Equip.
T2 | C50 | MEC_Uninsulated Pipes and Acc | ELE_Small Devices | NL-C50-MEC_Uninsulated Pipes and Acc vs ELE_Small Devices
T2 | C50 | MEC_Uninsulated Pipes and Acc | ELE_Services Lighting Fixtures | NL-C50-MEC_Uninsulated Pipes and Acc vs ELE_Services Lighting Fixtures
T2 | C50 | MEC_Uninsulated Pipes and Acc | FIR_Fire Pipes | NL-C50-MEC_Uninsulated Pipes and Acc vs FIR_Fire Pipes
T2 | C50 | MEC_Uninsulated Pipes and Acc | FIR_Sprinklers Heads | NL-C50-MEC_Uninsulated Pipes and Acc vs FIR_Sprinklers Heads
T2 | C50 | MEC_Uninsulated Pipes and Acc | FIR_Heat or Smoke Detectors | NL-C50-MEC_Uninsulated Pipes and Acc vs FIR_Heat or Smoke Detectors
0 | 0 | MEC_Uninulated Flexi duct | MEC_Uninulated Flexi duct | NL-0-MEC_Uninulated Flexi duct vs MEC_Uninulated Flexi duct
T2 | C50 | MEC_Uninulated Flexi duct | MEC_Equipment | NL-C50-MEC_Uninulated Flexi duct vs MEC_Equipment
T2 | C50 | MEC_Uninulated Flexi duct | ELE_Cable Tray and Fittings | NL-C50-MEC_Uninulated Flexi duct vs ELE_Cable Tray and Fittings
T2 | C50 | MEC_Uninulated Flexi duct | ELE_Conduit* | NL-C50-MEC_Uninulated Flexi duct vs ELE_Conduit*
T2 | C50 | MEC_Uninulated Flexi duct | ELE_Electrical Equip. | NL-C50-MEC_Uninulated Flexi duct vs ELE_Electrical Equip.
T2 | C50 | MEC_Uninulated Flexi duct | ELE_Small Devices | NL-C50-MEC_Uninulated Flexi duct vs ELE_Small Devices
T2 | C50 | MEC_Uninulated Flexi duct | ELE_Services Lighting Fixtures | NL-C50-MEC_Uninulated Flexi duct vs ELE_Services Lighting Fixtures
T2 | C50 | MEC_Uninulated Flexi duct | FIR_Fire Pipes | NL-C50-MEC_Uninulated Flexi duct vs FIR_Fire Pipes
0 | 0 | MEC_Uninulated Flexi duct | FIR_Sprinklers Heads | NL-0-MEC_Uninulated Flexi duct vs FIR_Sprinklers Heads
0 | 0 | MEC_Uninulated Flexi duct | FIR_Heat or Smoke Detectors | NL-0-MEC_Uninulated Flexi duct vs FIR_Heat or Smoke Detectors
0 | 0 | MEC_Equipment | MEC_Equipment | NL-0-MEC_Equipment vs MEC_Equipment
T3 | C50 | MEC_Equipment | ELE_Cable Tray and Fittings | NL-C50-MEC_Equipment vs ELE_Cable Tray and Fittings
T3 | C50 | MEC_Equipment | ELE_Conduit* | NL-C50-MEC_Equipment vs ELE_Conduit*
T3 | C50 | MEC_Equipment | ELE_Electrical Equip. | NL-C50-MEC_Equipment vs ELE_Electrical Equip.
T3 | C50 | MEC_Equipment | ELE_Small Devices | NL-C50-MEC_Equipment vs ELE_Small Devices
T3 | C50 | MEC_Equipment | ELE_Services Lighting Fixtures | NL-C50-MEC_Equipment vs ELE_Services Lighting Fixtures
T3 | C50 | MEC_Equipment | FIR_Fire Pipes | NL-C50-MEC_Equipment vs FIR_Fire Pipes
T3 | C50 | MEC_Equipment | FIR_Sprinklers Heads | NL-C50-MEC_Equipment vs FIR_Sprinklers Heads
T3 | C50 | MEC_Equipment | FIR_Heat or Smoke Detectors | NL-C50-MEC_Equipment vs FIR_Heat or Smoke Detectors
T3 | C150 | ELE_Cable Tray and Fittings | ELE_Cable Tray and Fittings | NL-C150-ELE_Cable Tray and Fittings vs ELE_Cable Tray and Fittings
T3 | C50 | ELE_Cable Tray and Fittings | ELE_Conduit* | NL-C50-ELE_Cable Tray and Fittings vs ELE_Conduit*
T3 | C50 | ELE_Cable Tray and Fittings | ELE_Electrical Equip. | NL-C50-ELE_Cable Tray and Fittings vs ELE_Electrical Equip.
T3 | C50 | ELE_Cable Tray and Fittings | ELE_Small Devices | NL-C50-ELE_Cable Tray and Fittings vs ELE_Small Devices
T3 | C50 | ELE_Cable Tray and Fittings | ELE_Services Lighting Fixtures | NL-C50-ELE_Cable Tray and Fittings vs ELE_Services Lighting Fixtures
T3 | C50 | ELE_Cable Tray and Fittings | FIR_Fire Pipes | NL-C50-ELE_Cable Tray and Fittings vs FIR_Fire Pipes
T3 | C50 | ELE_Cable Tray and Fittings | FIR_Sprinklers Heads | NL-C50-ELE_Cable Tray and Fittings vs FIR_Sprinklers Heads
T3 | C50 | ELE_Cable Tray and Fittings | FIR_Heat or Smoke Detectors | NL-C50-ELE_Cable Tray and Fittings vs FIR_Heat or Smoke Detectors
0 | 0 | ELE_Conduit* | ELE_Conduit* | NL-0-ELE_Conduit* vs ELE_Conduit*
T3 | C50 | ELE_Conduit* | ELE_Electrical Equip. | NL-C50-ELE_Conduit* vs ELE_Electrical Equip.
T3 | C50 | ELE_Conduit* | ELE_Small Devices | NL-C50-ELE_Conduit* vs ELE_Small Devices
T3 | C50 | ELE_Conduit* | ELE_Services Lighting Fixtures | NL-C50-ELE_Conduit* vs ELE_Services Lighting Fixtures
T3 | C50 | ELE_Conduit* | FIR_Fire Pipes | NL-C50-ELE_Conduit* vs FIR_Fire Pipes
T3 | C50 | ELE_Conduit* | FIR_Sprinklers Heads | NL-C50-ELE_Conduit* vs FIR_Sprinklers Heads
T3 | C50 | ELE_Conduit* | FIR_Heat or Smoke Detectors | NL-C50-ELE_Conduit* vs FIR_Heat or Smoke Detectors
0 | 0 | ELE_Electrical Equip. | ELE_Electrical Equip. | NL-0-ELE_Electrical Equip. vs ELE_Electrical Equip.
T3 | C50 | ELE_Electrical Equip. | ELE_Small Devices | NL-C50-ELE_Electrical Equip. vs ELE_Small Devices
T3 | C50 | ELE_Electrical Equip. | ELE_Services Lighting Fixtures | NL-C50-ELE_Electrical Equip. vs ELE_Services Lighting Fixtures
T2 | C50 | ELE_Electrical Equip. | FIR_Fire Pipes | NL-C50-ELE_Electrical Equip. vs FIR_Fire Pipes
T3 | C50 | ELE_Electrical Equip. | FIR_Sprinklers Heads | NL-C50-ELE_Electrical Equip. vs FIR_Sprinklers Heads
T3 | C1500 | ELE_Electrical Equip. | FIR_Heat or Smoke Detectors | NL-C1500-ELE_Electrical Equip. vs FIR_Heat or Smoke Detectors
T3 | C50 | ELE_Small Devices | ELE_Small Devices | NL-C50-ELE_Small Devices vs ELE_Small Devices
T3 | C50 | ELE_Small Devices | ELE_Services Lighting Fixtures | NL-C50-ELE_Small Devices vs ELE_Services Lighting Fixtures
T3 | C50 | ELE_Small Devices | FIR_Fire Pipes | NL-C50-ELE_Small Devices vs FIR_Fire Pipes
T3 | C50 | ELE_Small Devices | FIR_Sprinklers Heads | NL-C50-ELE_Small Devices vs FIR_Sprinklers Heads
T3 | C50 | ELE_Small Devices | FIR_Heat or Smoke Detectors | NL-C50-ELE_Small Devices vs FIR_Heat or Smoke Detectors
T3 | C50 | ELE_Services Lighting Fixtures | ELE_Services Lighting Fixtures | NL-C50-ELE_Services Lighting Fixtures vs ELE_Services Lighting Fixtures
T3 | C50 | ELE_Services Lighting Fixtures | FIR_Fire Pipes | NL-C50-ELE_Services Lighting Fixtures vs FIR_Fire Pipes
T3 | C50 | ELE_Services Lighting Fixtures | FIR_Sprinklers Heads | NL-C50-ELE_Services Lighting Fixtures vs FIR_Sprinklers Heads
T3 | C50 | ELE_Services Lighting Fixtures | FIR_Heat or Smoke Detectors | NL-C50-ELE_Services Lighting Fixtures vs FIR_Heat or Smoke Detectors
0 | 0 | FIR_Fire Pipes | FIR_Fire Pipes | NL-0-FIR_Fire Pipes vs FIR_Fire Pipes
T2 | C50 | FIR_Fire Pipes | FIR_Sprinklers Heads | NL-C50-FIR_Fire Pipes vs FIR_Sprinklers Heads
T2 | C50 | FIR_Fire Pipes | FIR_Heat or Smoke Detectors | NL-C50-FIR_Fire Pipes vs FIR_Heat or Smoke Detectors
T3 | HC | FIR_Sprinklers Heads | FIR_Sprinklers Heads | NL-HC-FIR_Sprinklers Heads vs FIR_Sprinklers Heads
T3 | C1500 | FIR_Sprinklers Heads | FIR_Heat or Smoke Detectors | NL-C1500-FIR_Sprinklers Heads vs FIR_Heat or Smoke Detectors
T3 | HC | FIR_Heat or Smoke Detectors | FIR_Heat or Smoke Detectors | NL-HC-FIR_Heat or Smoke Detectors vs FIR_Heat or Smoke Detectors

## Clash Matrix Legend
NL Clash Matrix Legend
Clash Status | Description | Comment
Blocker | The clash to be raised and assigned to either the lead consultant or BIM partners.
CR (Critical)
MA (Major) | Clash classified as Major, but can be resolved during construction. | Pipework > 50mm is graded as a Major Priority, < 50mm is graded as a Minor Priority in Revizto Clash Automation.
Mi (Minor) | Clash classified as Minor, but can be resolved during construction. | Pipework > 50mm is graded as a Major Priority, < 50mm is graded as a Minor Priority in Revizto Clash Automation.
Trivial | False positive. Not a real clash, can be ignore during clashing (Flex pipes...)
Clearance Matrix Legend
C50 | Clearance set 50mm | Vertical and Horizontal Clearance
C100V | Clearance set 100mm vertical only, Horizontal 50mm as default
C150V | Clearance set (150mm) vertical only Horizontal 50mm as default
HC | Hard Clash, 0mm Tolerance
CXXXV | Clearance set (project Specific) vertical only Horizontal 50mm as default
Clash Task Priority
T1 | Clash Task Scope #1 BIM team to be briefed what's the first major clash tasks to be done as per project timeline. | For example: Concrete work Underground Drainage Work Civil Steel work
T2 | Clash Task Scope #2 as per project timeline. | For example: Services walkway Access panel Fire rated timber framed wall Fire Damper Ceiling Pipework Above Ground Duct work Above Ground
T3 | Clash Task Scope #3 as per project timeline. | For example: Seismic Secondary framing Accessible pathway
T4 | Clash Task Scope #4 as per project timeline. | For example: Fitout
T5 | Additional Task outside template | Required manual added onto Revizto Clash Automation

## Item Categories
No. | Discipline | Element Name | Full Description | Comment
01 | Architecture | ARC_Columns* | Architectural Columns* | Architectural might include column element, worth checking the column locations vs Structural columns'
01 | Architecture | ARC_Ceiling | Ceiling
01 | Architecture | ARC_Doors* | Doors* | Need to considering modelling clearence zone aronud door. If not, the services walkway clerance zone to be modelling
01 | Architecture | ARC_Gen Model & Casework* | Generic Model & Casework* | Contain Seismic modelling. Further note. BEP to be clearly define the modelling practice. All Casework and generic modelling to be defined clearlly with workset. Including Lift door openings, channel drain
01 | Architecture | ARC_Roof | Roof
01 | Architecture | ARC_Fire & Acoustic Wall | Steel & Timber Framed Walls (Fire & Acoustic Wall)
01 | Architecture | ARC_Windows | Windows
01 | Architecture | ARC_Services Walkway | Special Items Services walk ways | Services walkway to be model if the consultant models have not included
01 | Architecture | ARC_Accessible Path | Special Items Accessible Walk Path | ie, Fire Escaping Path
04 | Services | SRV_Access Panel | Access Panel | fitting access point ie, ceiling access panel
01 | Architecture | ARC_Lighting Fixtures | Lighting Fixtures
01 | Architecture | ARC_Plumbing Fixtures | Plumbing Fixtures | Final procurement schedule to be checked to confirm the installation clearance and requirement. 1. Secondary frame packing 2. pipe feeds location
01 | Architecture | ARC_SOG Floor Insulation | Slab on Grade Insulation | Sometimes, the structural model does not show the insulation and barely identifies any service clashes that could affect the slab buildup
02 | Structural | STR_Seismic Elements | Seismic Elements
02 | Structural | STR_Conc work Excl Floor Slab | Structural - Concrete work Excluding Floor Slab
02 | Structural | STR_Steelwork (Bracing and Columns) | Structural - Steelwork (Bracing and Columns)
02 | Structural | STR Floor | Structural Floor
03 | Services - Plumbing and Drainage | HYD_Uninsulated Pipes and Acc | Pipe, Accessories and Fittings - HYD (Including Flexi and UnInsulated)
03 | Services - Plumbing and Drainage | HYD_Pipe Insulation | Pipe Insulation only
03 | Services - Plumbing and Drainage | HYD_Uninsulated Hot and Cold Pipes and Acc | Pipe, Accessories and Fittings - HOT AND COLD (Excl Flexi and Insulated)
03 | Services - Plumbing and Drainage | HYD_Hot and Cold Insulation | Pipe Insulation Only
03 | Services - Plumbing and Drainage | HYD_Plumbing Fixture | HYD_Plumbing Fixture
04 | Services - Mechanical | MEC_Air Terminals | Air Terminals
04 | Services - Mechanical | MEC_Uninsulated Duct and Acc | Uninsulated Duct, accessories and Duct Fittings (Excl Flexi) | Valves
04 | Services - Mechanical | MEC_Duct Insulation | Duct Insulation
04 | Services - Mechanical | MEC_Pipe Insulation | Insulated Pipe, Accessories and Fittings
04 | Services - Mechanical | MEC_Uninsulated Pipes and Acc | Uninsulated Pipe, Accessories and Fittings
04 | Services - Mechanical | MEC_Uninulated Flexi duct | Flexi Ducts with no insulation
04 | Services - Mechanical | MEC_Equipment | Mechanical Equipment | Final procurement schedule to be checked to confirm the installation clearance
05 | Services - Electrical | ELE_Cable Tray and Fittings | Cable Tray, Fittings
05 | Services - Electrical | ELE_Conduit* | Conduit* | Underground conduit to inground foundation beam
05 | Services - Electrical | ELE_Electrical Equip. | Electrical Equipment | Final procurement schedule to be checked to confirm the installation clearance
05 | Services - Electrical | ELE_Small Devices | Fire Device, Comms Devices, Security Devices, Electrical, Lighting Switches, Nurse Devices & Electrical Fixture* | The items are categories as small face based fixtures. Suggest to use Tag to identify who need to assign to.
05 | Services - Electrical | ELE_Services Lighting Fixtures | Services Lighting Fixtures | The final procurement schedule should be reviewed to verify installation clearances and ensure the allowed product depth.
06 | Services - Fire | FIR_Fire Pipes | Pipe, Accessories and Fittings - FIRE- (Including Flexi and Insulated)
06 | Services - Fire | FIR_Sprinklers Heads | Sprinklers Heads
06 | Services - Fire | FIR_Heat or Smoke Detectors | Fire Heating or Smoke Detectors

## Seismic Restraints Technical
Table 15, NZS4219:2009 | Minimum Clearances (mm)
Condition - Being Considered | Horizontal | Vertical
Unrestained components to unrestained components | 250 | 50
Unrestained components to restained components | 150 | 50
Restained components to restained components | 50 | 50
Penetration through structure (such as walls and floors) | 50 | 50
Note: Ceiling hangers and braces are considered to be restrained components for the purpose of this table
Notes:
Rigid ductwork, where the hanger length from the top of the duct to the structure support exceeds 200mm shall be restrained against seismic forces.
Pipework exceeding 50mm in diameter and located more than 150mm from the structural support shall be laterally braced. The spacing of transverse and longitudinal bracing shall be in accordance with nzs 4219, section 3.6.
Equipment within the ceiling exceeding 10kg mass shall be independently fixed and braced to the structure and separated from the ceiling by 25mm all around to allow for independent movement between equipment and ceiling
Clearance of services at all penetrations through structure or partition walls shall be 12mm for ductwork, 15mm for pipework and 25mm for cable tray. All services shall be restrained at penetrations through structure and partition walls. The design engineer of the structure / partition walls shall ensure the structure / partition walls shall be capable of resisting lateral seismic load imposed on it due to restraint provided at the penetrations
Piping systems (NZS 4219, Section 5.8)
Ducting (Section 5.9)
Suspended equipment (Section 5.13)
Floor-mounted components (Section 3.7)
Physical interference: Ensure that seismic restraints, such as braces or fixings, do not interfere with the routing of pipes or ducts.
Clearance and access: Check that adequate clearances are maintained around seismic restraints and that access for maintenance or inspection remains unimpeded (as per Section 5.15 for plinths and clearances).
Load path conflicts: Ensure the load paths for seismic restraints are clear and do not intersect with other building systems, as per the requirements in Section 2 (General Requirements)
Where pipe restraints are not required
Where duct restraints are not required
Where electrical services support system (cable tray) restraint is and is not needed.

## #7 Notes (hidden)
Architecture | Flexbile
Structure
Gravity Pipework
Mechanical
Electrical
Fire | More Flexible